## Economic Values
Economic Activity By Segment, 2006
Employment
HVAC in non-residential Buildings | >95,000
Domestic Air-conditioning | >15,990
Cold Storage | ~5620
Drivers of Refrigerated Transport | ~16,400
Auto Air | > 24,000
TOTAL ESTIMATED DIRECT EMPLOYMENT | ~ 157,000
Expenditure
HVAC in non-residential Buildings | ~$7,100,000,000
Installed cost of airconditioning equipment (exluding gas ducted heating) Exl GST | 3661067042.7273
Estimated Expenditure on Domestic Refrigerators and Freezers | 747217018.1078
Wages for employees other than in HVAC for non-residential buildings | ~$3,201,494,000
Bulk Gas Imports | ~
Energy Spend (exluding non-residential HVAC) | ~ $1,248,160,000
TOTAL ESTIMATED DIRECT SPENDING | ~ $15,957,938,061
Note on B3: 2006 estimate by Energy Strategies includes workforce along the supply chain for HVAC services in non-residential building and including maintenance personnel but does not include facilities managers. This estimate was intended to cover specialist close control and large chiller enterprises.
Note on B4: See comment at cell G13, Worksheet: 'AC Summary. This estimate is based on the assumption that for every person directly employed installing systems there is at least another .5 of a person employed in admin, sales, maintenance and ancillary services in the domestic airconditioning industry that is not involved in the non-residential industry
Note on B5: Swire's, with ~21% of all estimated cold storage employs 1200 people.
Note on B6: Estimate one full time driver for every refrigerated vehicle
Note on B7: Approximately 16,000 individuals have been licenced under the Australian Refrigeration Council licensinig scheme to work on mobile systems, approximately 14,000 busineses have applied for Trading Authorisations to purchase and handle bulk refrigerant gases. This estimate assumes that for every licenced technician there is another .5 of a person employed directly in admin, sales and ancillary services in the vehicle airconditioning industry
Note on B12: 2006 estimate by Energy Strategies of the value of the 'Climate Control' industry includes the 'energy spend', cost of new systems, maintenance and replacement parts on existing systems and engineering consulting.
Note on B13: See Worksheet: 'AC Summary'
Note on B14: See Worksheet: 'Domestic Appliances'
Note on B15: 62,000 multiplied by 2006 adult annual average wage $51,637
Note on B16: Waiting on value
Note on B17: @$0.08c kWh, some commercial applications caught up here pay as little as $0.045c/kWh but residential and others will pay as high as $0.14c/kWh
COMMENTARY
Because there are several areas for which there is simply not sufficient data to make any reasonable deductions at this point, these numbers are likely to be somewhat conservative.
It is felt that all of the major areas of employment and expenditure are captured here, although estimates of employment are thought to be conservative. However there are significant specialist areas for which insufficient data is presently available and which could add materially to these conclusions.
Major specialist areas for employment, sales of technology, engineering services and economic activity for which we presently have no certainty that we have collected accurate data includes:
- Sales, service and installation of small cool rooms - not in the cold chain and supermarkets
- Commercial Aviation - domestic and international flights serviced here
- Mining and in mine machinery
- Marine Systems - domestic, international, commercial and private vessels equipped and serviced here
- Ancillary sales and service for control systems, sensors, filters, chemicals, specialist cleaning
- Military vehicles, equipment and systems

## Installed Base of Machinery
Estimates of Installed Base of Various Machinery by Segment, 2006
Domestic Refrigerators and Freezers | 13000000
Domestic and Small Commercial Airconditioning | 5638668.5501
Chillers | 22450
Volume of Cold Storage | 9,460,000 m3
Number of Supermarket Cold Store installations | 3675
Farm, Catering and Shop Coolrooms | 22853
Self Contained Commercial Refrigeration Equipment | 821500
Refrigerated Vehicles | 16418.0763
Passenger Vehicles with Airconditioning | 10293770
Note on A2: See Worksheet: 'Domestic Appliances'
Note on A3: See Worksheet: 'AC per Household', cell I12 and Worksheet: 'AC Summary', column N.
Note on A4: See Worksheet: 'Chillers', cell F77
Note on A5: See Worksheet: 'CC-Cold Storage'
Note on A6: See Worksheet: 'CC-Supermarket', cell G8
Note on A7: See Worksheet: 'CC-Coolrooms' Row 9. This figure exludes Supermarket and Cold Chain
Note on A8: See Worksheet: CC-Merch
Note on A9: See Worksheet: 'CC-Ref Transport'
Note on A10: See Worksheet: 'Auto Air'

## Energy & GHG All Refrig. Cycles
Energy Consumption & Emissions by Segment | Energy Consumption GWh/a | Fuel combustion (scope 1) and/or electricity (scope 2) emissions Mt CO2-e pa
Air Conditioning: Domestic | 5247.6794 | 4.6862
Split Systems | 1244.212 | 1.1111
Wall Hung Split Systems | 3061.4848 | 2.7339
Window/Wall | 868.8345 | 0.77587
Refrigerated Portable | 73.1481 | 0.065321
Air Conditioning: Commercial | 17437.1099 | 15.5713
RT Packaged | 2567.1475 | 2.2925
Chillers | 4775.1687 | 4.2642
Split Systems | 4966.1596 | 4.4348
Wall Hung Split Systems | 3555.0472 | 3.1747
Window/Wall | 217.2086 | 0.19397
Precision Control A/C | 1108.6875 | 0.99006
VRV Systems | 247.6908 | 0.22119
Cold Food Chain | 10773.3623 | 9.6206
Chillers | 1688.8481 | 1.5081
Industrial Refrigeration (Ammonia) | 356 | 0.31791
Cold/Freezer Rooms: Remote (excl. Cold Storage Channel/Superarket) | 315.9767 | 0.28217
Cold Storage (Channel) | 462.1375 | 0.41269
Supermarket | 5270.4 | 4.7065
Pubs/Clubs/Convenience Stores/Take Away Food | -
Merch Cabinets & Vend Machines: Self Cont. | 2680 | 2.3932
Transport | -
Other Refrig. Cycle Equip. | 2111.0601 | 1.8852
Chillers in Industrial Applications | 2111.0601 | 1.8852
Misc. (water coolers, heat-pump swimming pools, etc.) | -
Auto Air (excl. Train/Marine/Aviation/Defence) | - | 1.8604
Domestic Refrigeration | 9470 | 8.4567
Total Energy Consumption in GWh/pa and GHG Mt CO2-e pa | 45039.2117 | 40.22
Note: Expand Tabs on left hand of screen for detail.
Data highlighted in blue throughout spread-sheet could benefit from further investigation to improve accuracy of estimates.
Note on A17: Refer notes on Industrial Refrigeration tab
Note on B31: This is equivalent to 21.9% of all electricity sent out from Australian generators in 2005/06 of 194,781 GWh - NEMMCO 2006 Annual Report
Note on C7: In 2006 a project undertaken by Energy Strategies to estimate emissions from HVAC systems in non-residential buildings arrived at a conservative lower estimate of 21.9Mt pa of CO2-e to an upper estimate of 25.5Mt pa CO2-e from HVAC systems using a top down approach. That estimate included the energy used in fans for airhandling and ventilation. The figure arrived at here is a calculation of the energy consumed in the refrigerative cooling equipment of HVAC systems, and does not include fan energy. However using the rule of thumb that energy used in fans for airhandling and ventilation is arouond 60% of cooling energy then the two estimates reconcile well. Multiply the value at C7 x 1.6 = 25.2 Mt pa of CO2-e
Note on C31: Not including auto air at C15 due, stationary sources only. This is equal to 7% of all greenhouse gas emissions from all sources in Australia in the year to June 2006 based on Energy Strategies Prompt Indicators value of 571.9 Mt of CO2e for Australian emissions 2005/06
Refrigeration technology consumed about 15% of all electricity consumed worldwide, Coulomb, D. 2005. A word from the director. Int. J. Refrig. 25: 973-976.

## AC Energy Calc
Air Conditioning Energy Calculations (kWh/a)
| QLD | NSW & ACT | VIC | TAS | SA | NT | WA | Total
|  | & ACT |  |  | & BH
WHS Systems Residential
Cooling Hrs | 600 | 180 | 100 | 50 | 200 | 2000 | 300 | -
Heating Hrs | 100 | 300 | 350 | 450 | 250 | 0 | 150 | -
% Units by location | 30.2% | 28% | 19.9% | 1.8% | 6.4% | 2% | 11.7% | 100%
Existing Stock | 751074 | 696360 | 494913 | 44766 | 159168 | 49740 | 290979 | 2487000 | 2487000
Total Cooling Hrs | 450644400 | 125344800 | 49491300 | 2238300 | 31833600 | 99480000 | 87293700 | 846326100
Total Heating Hrs | 75107400 | 208908000 | 173219550 | 20144700 | 39792000 | 0 | 43646850 | 560818500
Cooling Energy kWh/a | 1022616138.4615 | 284436276.9231 | 112307180.7692 | 5079219.2308 | 72237784.6154 | 225743076.9231 | 198089550 | 1920509226.9231
Heating Energy kWh/a | 152804710.3448 | 425019724.1379 | 352412187.931 | 40984044.8276 | 80956137.931 | 0 | 88798763.7931 | 1140975568.9655
WHS System Res kWh/a | 1175420848.8064 | 709456001.061 | 464719368.7003 | 46063264.0584 | 153193922.5464 | 225743076.9231 | 286888313.7931 | 3061484795.8886
WHS System: Commercial
Effective Operating Hrs/day | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | -
Ratio Cooling to Heating | 0.85714 | 0.375 | 0.22222 | 0.1 | 0.44444 | 1 | 0.66667 | -
% Units by location | 30.2% | 28% | 19.9% | 1.8% | 6.4% | 2% | 11.7% | 100%
Existing Stock | 250358 | 232120 | 164971 | 14922 | 53056 | 16580 | 96993 | 829000
Total Running Hrs/a | 498024651.5 | 461744710 | 328168561.75 | 29683588.5 | 105541648 | 32981765 | 192943325.25 | 1649088250
WHS System Comm kWh/a | 1111806384.1595 | 977325126.0987 | 683362769.7618 | 61022011.2021 | 225070743.3253 | 74843235.9615 | 421616895.9167 | 3555047166.4255 | 6616531962.3141
Window/Wall Units Residential & Commercial
Cooling Hrs | 600 | 180 | 100 | 50 | 200 | 2000 | 300 | -
% Units by location | 30.2% | 28% | 19.9% | 1.8% | 6.4% | 2% | 11.7% | 100%
Existing Stock | 674668 | 625520 | 444566 | 40212 | 142976 | 44680 | 261378 | 2234000
Existing Stock: Residential | 539734.4 | 500416 | 355652.8 | 32169.6 | 114380.8 | 35744 | 209102.4 | 1787200
Total Cooling Hrs | 404800800 | 112593600 | 44456600 | 2010600 | 28595200 | 89360000 | 78413400 | 760230200
Window/Wall Units kWh/a | 578286857.1429 | 160848000 | 63509428.5714 | 2872285.7143 | 40850285.7143 | 127657142.8571 | 112019142.8571 | 1086043142.8571
Portable
Cooling Hrs | 600 | 180 | 100 | 50 | 200 | 2000 | 300 | -
% Units by location | 30.2% | 27.99% | 19.94% | 1.781% | 6.363% | 2.061% | 11.66% | 100%
Existing Stock | 63428.6844 | 58774.8461 | 41866.4244 | 3741.0321 | 13362.934 | 4327.8646 | 24488.258 | 210000
Total Cooling Hrs | 38057210.6422 | 10579472.2898 | 4186642.4425 | 187051.6047 | 2672586.7964 | 8655729.1242 | 7346477.4122 | 71685170.312
Portable kWh/a | 38833888.4104 | 10795379.8876 | 4272084.125 | 190868.9844 | 2727129.3841 | 8832376.6573 | 7496405.5226 | 73148132.9714
Split Systems: Residential
Cooling Hrs | 600 | 180 | 100 | 50 | 200 | 2000 | 300 | -
Heating Hrs | 100 | 300 | 350 | 450 | 250 | 0 | 150 | -
% Units by location | 22.64% | 35.68% | 13.41% | 2.044% | 11.56% | 1.334% | 13.35% | 100%
Existing Stock | 94843.7122 | 149481.6973 | 56182.7848 | 8565.9539 | 48417.9974 | 5588.9175 | 55918.9369 | 419000
Total Cooling Hrs | 56906227.3227 | 26906705.5128 | 5618278.4827 | 428297.6974 | 9683599.47 | 11177835.0388 | 16775681.0571 | 127496624.5816
Total Heating Hrs | 9484371.2205 | 44844509.188 | 19663974.6896 | 3854679.2767 | 12104499.3375 | 0 | 8387840.5285 | 98339874.2408
Cooling Energy kWh/a | 328305157.6311 | 155230993.3432 | 32413145.0927 | 2470948.2543 | 55866920.0194 | 64487509.8392 | 96782775.3294 | 735557449.5093
Heating Energy kWh/a | 49057092.5196 | 231954357.8691 | 101710213.9115 | 19937996.2587 | 62609479.3321 | 0 | 43385382.0442 | 508654521.9352
Split System: Res kWh/a | 377362250.1507 | 387185351.2123 | 134123359.0042 | 22408944.513 | 118476399.3515 | 64487509.8392 | 140168157.3736 | 1244211971.4445
Split Systems: Commercial
Effective Operating Hrs/day | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | -
Ratio Cooling to Heating | 0.85714 | 0.375 | 0.22222 | 0.1 | 0.44444 | 1 | 0.66667 | -
% Units by location | 22.64% | 35.68% | 13.41% | 2.044% | 11.56% | 1.334% | 13.35% | 100%
Existing Stock | 94843.7122 | 149481.6973 | 56182.7848 | 8565.9539 | 48417.9974 | 5588.9175 | 55918.9369 | 419000
Total Running Hrs/a | 205653154.1014 | 324126732.4346 | 121823225.1498 | 18573877.0276 | 104986547.2247 | 12118658.0445 | 121251113.7674 | 908533307.75
Split System: Comm kWh/a | 1167220604.3592 | 1744179726.1054 | 644946486.087 | 97076012.3395 | 569204171.7004 | 69915334.8721 | 673617298.7078 | 4966159634.1714 | 6210371605.6159
VRV System
Effective Operating Hrs/day | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | -
Ratio Cooling to Heating | 0.85714 | 0.375 | 0.22222 | 0.1 | 0.44444 | 1 | 0.66667 | -
% Units by location | 22.64% | 35.68% | 13.41% | 2.044% | 11.56% | 1.334% | 13.35% | 100%
Existing Stock | 2240.9374 | 3531.9065 | 1327.4691 | 202.3937 | 1144.0052 | 132.0532 | 1321.235 | 9900
Total Running Hrs/a | 4859107.937 | 7658364.3224 | 2878400.7852 | 438857.715 | 2480589.0633 | 286335.8345 | 2864883.1177 | 21466538.775
VRV System KWh/a | 56066630.0423 | 88365742.182 | 33212316.7519 | 5063742.8651 | 28622181.4997 | 3303875.013 | 33056343.6652 | 247690832.0192
RT Package
Effective Operating Hrs/day | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | -
% Cooling to Heating | 0.85714 | 0.375 | 0.22222 | 0.1 | 0.44444 | 1 | 0.66667 | -
% Units by location | 23.3% | 21.68% | 32.1% | 0.5501% | 7.654% | 2.199% | 12.53% | 100%
Existing Stock | 15934.7781 | 14827.2308 | 21953.8786 | 376.296 | 5235.3737 | 1503.7931 | 8568.6498 | 68400
Total Running Hrs/a | 34551972.9727 | 32150436.771 | 47603412.6429 | 815936.599 | 11352055.8132 | 3260730.6407 | 18579722.4606 | 148314267.9
RT Package kWh/a | 622309048.3519 | 549008355.2638 | 799737332.4006 | 13532607.0075 | 195310068.6891 | 59696453.2674 | 327553625.6022 | 2567147490.5824
Precision A/C
Effective Operating Hrs/day | 13 | 13 | 13 | 13 | 13 | 13 | 13 | -
% Units by location | 19.4% | 35% | 24.7% | 2.4% | 7.6% | 1% | 9.9% | 100%
Existing Stock | 2619 | 4725 | 3334.5 | 324 | 1026 | 135 | 1336.5 | 13500
Total Running Hrs/a | 12427155 | 22420125 | 15822202.5 | 1537380 | 4868370 | 640575 | 6341692.5 | 64057500
Precision A/C kWh/a | 215085375 | 388040625 | 273845812.5 | 26608500 | 84260250 | 11086875 | 109760062.5 | 1108687500
Chillers < 530 kW
Effective Operating Hrs/day | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | -
% Units by location | 19.4% | 35% | 24.7% | 2.4% | 7.6% | 1% | 9.9% | 100%
Existing Stock | 562.6 | 1015 | 716.3 | 69.6 | 220.4 | 29 | 287.1 | 2900
Total Running Hrs/a | 1219906.5369 | 2200862.3087 | 1553179.9722 | 150916.2726 | 477901.5299 | 62881.7803 | 622529.6245 | 6288178.025
Chillers < 530 kW | 121631857.6447 | 219438918.4313 | 154861179.5786 | 15047240.121 | 47649593.7165 | 6269683.3838 | 62069865.4991 | 626968338.375
Chillers > & = 530 kW
Effective Operating Hrs/day | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | 5.9406 | -
% Units by location | 19.4% | 35% | 24.7% | 2.4% | 7.6% | 1% | 9.9% | 100%
Existing Stock | 1348.3 | 2432.5 | 1716.65 | 166.8 | 528.2 | 69.5 | 688.05 | 6950
Total Running Hrs/a | 2923569.1142 | 5274480.3606 | 3722276.1402 | 361678.6533 | 1145315.7355 | 150699.4389 | 1491924.4449 | 15069943.8875
Chillers > & = 530 kW | 804750866.6913 | 1451870120.3194 | 1024605484.9111 | 99556808.2505 | 315263226.1265 | 41482003.4377 | 410671834.0332 | 4148200343.7697
Chillers kWh/a | 926382724.3361 | 1671309038.7507 | 1179466664.4897 | 114604048.3715 | 362912819.843 | 47751686.8214 | 472741699.5323 | 4775168682.1447
Total by State | 6147142753.1145 | 6467074427.1301 | 4126334442.8132 | 374395044.9346 | 1732978378.3373 | 687047883.8285 | 2522848079.9716 | 22057821010.1299
% by State | 27.87% | 29.32% | 18.71% | 1.697% | 7.857% | 3.115% | 11.44% | 100%
Assumptions for Sensitivity Analyisis
| WHS System | Window/Wall | Refrig. Portable | Split System | VRV Systems | Precision AC | RT Package | Chillers < 530 kW | Chillers > & = 530 kW
EER | 2.6 | 2.45 | 2.45 | 2.6 | 2.6 | 2.6 | 2.6 | - | -
COP | 2.9 | - | - | 2.9 | 2.9 | - | 2.9 | 3.4 | 3.8
Av. Capacity kW | 5.9 | 3.5 | 2.5 | 15 | 30 | 45 | 47.6 | 339 | 1046
Existing Stock | 3316000 | 2234000 | 210000 | 838000 | 9900 | 13500 | 68400 | 2900 | 6950
% Commercial Applications | 25% | 20% | - | 50% | 100% | - | 100% | 100% | 100%
Commercial Applications
Split Systems, RT Package & Chillers |  |  |  | WHS Systems
Run Time | Business Mix | Equiv. Hrs/day | Weighted Av. Hrs | Run Time | Business Mix | Equiv. Hrs/day | Weighted Av. Hrs
24hrs/365days | 7.5% | 24 | 1.8 | 24hrs/365days | 0% | 24 | 0
12hrs/365days | 22.5% | 11.7 | 2.6325 | 12hrs/365days | 50% | 11.7 | 5.85
12hrs/252days | 70% | 8.3 | 5.81 | 12hrs/252days | 50% | 8.3 | 4.15
|  |  | 10.2425 |  |  |  | 10
Operating Capacity Bins | % Operating Time @ Capacity Level | Weighted Av. |  | Operating Capacity Bins | % Operating Time @ Capacity Level | Weighted Av.
100% | 1% | 1% |  | 100% | 40% | 40%
75% | 42% | 31.5% |  | 75% | 10% | 7.5%
50% | 45% | 22.5% |  | 50% | 10% | 5%
25% | 12% | 3% |  | 20% | 10% | 2%
0% | 0% | 0% |  | 0% | 30% | 0%
| 100% | 58% |  |  | 100% | 54.5%
Effective Operating Hrs/day | 5.9406 |  |  | Effective Operating Hrs/day | 5.45
Note on A1: The Av. energy consumption for residential air conditioners were: - WHS Systems = 473kWh/pa Split Systems = 901kWh/pa These av. energy consumption values are consistent with the range quoted by EES from 547kWh/pa to 698kWh/pa for residential applications in NSW. Refer 'Australian Residential Building Sector Greenhouse Gas Emissions 1999-2010' (EES 1999).
Note on A5: Hours of Air Conditioner Heating & Cooling use for Australian Capital Cities are the same as those used on www.energyrating.gov.au calculator, originally sourced based on EES estimates & ABS data & should be treated with caution.
Note on A7: Based on average units sold into regions - Informark data 2003 & 2006
Note on A11: Calculation based on: Av.EER = 2.6 Av. COP = 2.9 Av. Size = 5.9kW Informark data, 2003 rather than 5.4kW av. obtained in report below. In report Status of AC in Australia, EES, 2005 there was considerable analysis on EER/COP over the last 20 years. pp23 taken av. over last 10 yrs. EER/COP are based on ideal laboratory conditions, in the field other factors will lower efficiency by up to 30% (Humidity/Region, Incorrect charge, Poor unit evauation, Dirty filter, Poor system design, Poor installation). The Existing Stock ignores cooling only models, certainly the proportion sold in 2006 was a single digit % and diminishing rapidly with most suppliers electing to offer heatpump models only.
Note on A17: Based on average units sold into regions - Informark data 2003 & 2006
Note on A22: Only considered Cooling Hrs, used same hrs by regional as WHS Systems.
Note on A23: Same regional % as WHS Systems
Note on A27: Assumed Residential & Commercial operating behavior to be similar with Window/Wall Units
Note on A35: Hours of Air Conditioner Heating & Cooling use for Australian Capital Cities are the same as those used on www.energyrating.gov.au calculator, originally sourced based on EES estimates & ABS data & should be treated with caution.
Note on A37: Based on average units sold into regions - Informark data 2003 & 2006
Note on A47: Based on average units sold into regions - Informark data 2003 & 2006
Note on A54: Based on average units sold into regions - Informark data 2003 & 2006
Note on A60: Ratio of Cooling to Heating Hours are based on www.energyrating.gov.au calculator, originally sourced based on EES estimates & ABS data & should be treated with caution. This only effects ratio of EER to COP.
Note on A61: Based on average units sold into regions - Informark data 2005 & 2006
Note on A66: MEPS Close Control A/C - 2004, pp4 Average efficiency (EER) = 2.6 when operating at design conditions Units operate 24hrs/day, all year Approx. 50% of units installed operate as back up units & only operate if primary units fails or under extreme conditions
Note on A67: % Split by Population, ABS 2004
Note on A73: % Split by Population, ABS 2004
Note on A79: % Split by Population, ABS 2004
Note on A115: Methodology Checked with Mechanical Services Engineer from Commercial AC Services Sector
Note on A118: Hospitals, Industrial Factories, Nursing Homes
Note on A119: Shopping Centres Typical operation: 4 days, 8am to 9pm & 3 days, 8am to 6pm
Note on A120: Regular businesses that operate 5 days per week, excluding public holidays. System operates from 6.30am to 6.30pm, there is a trend towards 7am to 5pm
Note on A126: 20% of power = Fan only mode, need to check confirm with Engineering data
Note on B113: Ratio needs to be confirmed by major A/C players (Daikin, Fujitsu, etc.)
Note on B117: Best Guess only, recommend review of m2 of ea. segment for more accurate estimate
Note on B122: The part load performance for each of the assumed hours of operation was based on the part load operational criteria as set out in ARI 550/590.
Note on C6: Heating hours in Sydney = 200 Canberra = 500
Note on C36: Heating hours in Sydney = 200 Canberra = 500
Note on E113: Ratio needs to be confirmed by major A/C players (Daikin, Fujitsu, etc.)
Note on E118: Hospitals, Industrial Factories, Nursing Homes
Note on E119: Shopping Centres Typical operation: 4 days, 8am to 9pm & 3 days, 8am to 6pm
Note on E120: Regular businesses that operate 5 days per week, excluding public holidays. System operates from 6.30am to 6.30pm, there is a trend towards 7am to 5pm
Note on E126: 20% of power = Fan only mode, need to check confirm with Engineering data
Note on F117: Best Guess only, recommend review of m2 of ea. segment for more accurate estimate
Note on F122: Rough estimate only, require support with study
Note on I110: Efficiency can decline over time; - Wear & tear - Relative to new technology coming onto the market - Depends on maintenance & improvements
Note on J110: Efficiency can decline over time; - Wear & tear - Relative to new technology coming onto the market - Depends on maintenance & improvements
Energy Calculations & References:
Calculation method used was as follows:
Energy Consumed (Residential) = # Existing Stock in Region x Typical Run Hr in Region p.a. x Av. Capacity kWr/COP or EER
This calculation was undertaken for heating & cooling, total energy consumed was the sum of the two. Assumptions are noted in embedded comments & tables below
A similar method was used for commercial, however rather than run hours per region, an effective operating time per day was estimated x 365 days.
Other References
Energy Strategies, 2007, previous conservative estimates of Commercial Air Conditioning (based on top down approach) are 21.9 to 25.5 Mt CO2e pa. (approx. 62.8PJ = 17,452GWh/a to 73.2PJ = 20,321GWh/a).
MEPS AC, 2002 pp 10. According to recent studies, airconditioning is estimated to represent approximately (approx. 3.4PJ = 956 GWh/a) 1.2Mt CO2-e for the residential sector and (approx. 70PJ = 19,444 GWh/a) 24.4Mt CO2-e for the commercial sector in 2000.
Status of AC in Australia, 2005 pp 26. Annual energy savings in 2018 are projected to be 782 GWh per year with emissions down by about 0.61 Mt CO2-e per year; for total savings of 7,970 GWh and 6.2 Mt CO2-e. pp 32, estimate Energy consumption of Air Conditioners in 2004 to be 4.6 PJ (1278 GWh/a) in the residential sector, data did not take into account any MEPS reductions. These two pieces of data from same report appear to contradict???
MEPS Close Control AC, 2004 pp4. It is estimated that approximately 3000 roof top packaged air conditioners are sold each year in Australia (over 18kWr), with the average size of 60 kWr (PB closer to 45kW, same as precision). Hence the market for close control air conditioners is approximately 15% of this total market (PB closer to 20%). This makes close control air conditioners relatively significant in terms of energy usage as the average utilization of close control air conditioners is typically 2 to 4 times (PB our analysis used 2.4 times) more than comfort air conditioners. Hence, energy consumption from close control air conditioners could be 10 to 20 % (PB 20% x 2.4 = 48%, close control is more significant) of the energy usage attributed to package air conditioners.
MEPS Heatpumps - 2004, pp 2
Energy consumption from heat pumps in 2002 is estimated to be over 600 GWh/a and forecast to grow to 1,100 GWh in 2010. Heat pumps are typically replacing electric resistive heating and solid fuel heaters as the main heating source.

## AC Summary
Product Type | Av. Size Cooling (kW) | Quantity (Units) p.a. | NomimalGrowth (%) | Av. Value | Av. Man Hrs per Install (Res & LC) | Total Man Hrs to Install (Res & LC) | Consumer Spend (Res & LC) Excl. GST | Est. Participation Rate | Est. Quantity Sold (Units) | Wholesale Value p.a. Excl. GST | Est. Imported (%) | Est. Av. Life (Yrs) | Existing Stock Equipment | Energy Consumption GWh/a | Existing Stock Refrigerant (Res & LC) (Tons)
[15 empty] | R22 | R407C | R410A
Split Systems | 15 | 133395 | 15% | 3188.8676 | 35 | 5187583.3333 | 1293527272.7273 | 90% | 148216.6667 | 472643333.3333 | 70% | 12 | 838000 | 6210.3716 | 3151 | 231 | 591
VRV Systems | 30 | 3000 | 25% | 17000 | - | - | - | 100% | 3000 | - | 100% | 15 | 9900 | 247.6908 | - | - | -
Wall Hung Split Systems | 5.9 | 655500 | 20% | 1050 | 12 | 10488000 | 1870360000 | 75% | 874000 | 917700000 | 100% | 10 | 3316000 | 6616.532 | 4227.9 | - | 1244
Window/Wall Units | 4.5 | 166807 | Decline | 450 | 6 | 944382 | 221929770 | na | 157397 | 70828650 | 100% | 12 | 2234000 | 1086.0431 | 1877 | - | -
RT Packaged | 47.6 | 4675 | 1% | 8252 | - | - | - | 90% | 5194.4444 | - | 40% | 20 | 68400 | 2567.1475 | - | - | -
Evaporative Coolers | 14 | 70000 | Decline | 1100 | 18 | 1260000 | 252000000 | na | 70000 | 77000000 | 10% | 13 | 823000 | - | na | na | na
Gas Ducted Heaters | 23.5 | 62217 | 6% | 1200 | 24 | 1571797.8947 | 209573052.6316 | 95% | 65491.5789 | 78589894.7368 | 15% | 15 | 675700 | - | na | na | na
Chillers < 530 kW | 339 | 192 | 7.5% | - | - | - | - | na | 192 | - | n.a. | 20 | 2900 | 626.9683 | - | - | -
Chillers > & = 530 kW | 1046 | 415 | 7.5% | - | - | - | - | na | 415 | - | n.a. | 25 | 6950 | 4148.2003 | - | - | -
Refrigerated Portable | 2.5 | 30000 | 10% plus | 440 | 0 | - | 23250000 | na | 30000 | 13200000 | 100% | 7 | 210000 | 73.1481 | 74 | - | 32
Precision Control A/C | 45 | 960 | 5% | 35000 | - | - | - | na | 960 | - | 95% | 15 | 13500 | 1108.6875 | - | - | -
[6 empty] | 19451763.2281 | 3870640095.3589 |  |  | 1629961878.0702 |  |  |  | 22684.7893 | 9329.9 | 231 | 1867
Miscellaneous:
Heat Pump Swimming Pool | 18 | 900 | 4% | - | - |  |  | na | - |  | ? | 10 | 9000
Note on A1: The statistical Data was collected via industry sources & used in conjunction with import data from DEH & Import statistics from ABS. Industry gain acurate information as follows: - Market leaders with a significant share & years of experience have a good understanding of market sizes/details by product category - Unit volumes & typical sizes are estimated at industry gatherings such as MEPS committes - Several product categories are recorded by Informark, this information is only available to members that subscribe, participants can estimate total market data by estimating participation rate
Note on A3: Applications: Domestic & Commercial Trends: Inverter technology & R410A Key Equipment Suppliers: Daikin - Market Leader Mitsubishi Electric Fujitsu General ECP/Airwell Hitachi Australia LG Electronics Panasonic Mitsubishi Heavy Industries Trane Lennox Samsung Sanyo Dunnair Ascon Bonaire Derby Cooline Chinese mfrs inc. Gree/Midea/Haier/Chigo/Chunlan Locally Manufactured Actron Air Temperzone Carrier/APAC Uniaire Ascent Air Pioneer For more comprehensive listing log onto: http://www.energyrating.gov.au/appsearch/air_srch.asp
Note on A4: Applications: Commercial VRV Systems - relatively new technology used in commercial applications, key equipment suppliers in Australia are Daikin, Mitsubishi Electric & other top tier suppliers with Japanese origins
Note on A5: Applications: Domestic & light Commercial (ie hospitality, small retail shops, medical practices) Trends: Inverter technology & R410A Top Tier Suppliers (Japanese Origins) Daikin - Market Leader Mitsubishi Electric Fujitsu General Toshiba (Carrier) Mitsubishi Heavy Industries Hitachi Australia Panasonic Second Tier Suppliers LG Electronics Sanyo ECP, Email Air Over 100 other suppliers (most source from other suppliers, predominantly in China) Electrolux Trane Lennox Samsung Dunnair Ascon Bonaire Derby Cooline Chinese mfrs inc. Gree/Midea/Haier/Chigo/Chunlan For more comprehensive listing log onto: http://www.energyrating.gov.au/appsearch/air_srch.asp
Note on A6: Old Technology, limited range that meets current MEPS standards, replaced by Wall Mounted Splits
Note on A7: Applications: Mostly Commercial & some large Residential Trends: R407C & VRV Systems Locally manufactured Temperzone Carrier/APAC Actron Air Accent Air Uniaire Imported Daikin Trane Mc Quay Mitsubishi Electric Mitsubishi Heavy Industries ECP Lennox York Dunnair Arena Hitachi Australia LG Electronics
Note on A8: Applications: Mostly Domestic, suited to regions with low Humidity, inexpensive to run, cheap to install for whole-house Trends: Shift towards wall mounted splits, inexpesive alternative Key Equipment Suppliers Brivis Bonaire Breezair Breamar Celair Stadt (in liquidation)
Note on A9: Applications: Mostly Domestic, requires natural gas, more expensive to operate on LPG, suited to Southern Region & Canberra (where greater demand for heating versus cooling) Trends: 5 Star condensing heaters Key Equipment Suppliers Brivis Breamar Vulcan Lennox Omega Stadt (in liquidation)
Note on A10: Applications: The main application is commercial HVAC, however chillers are used in a diverse range of applications including Brewing/Winemaking, Dairy Industry, Food Processing & a variety of industrial applications. Key Suppliers: Commercial AC - Carrier, Mc Quay, Trane York, Airwell, Cooline, Daikin, MTA, Champion Compressors Hitachi, Sharp & Pendry Local Manufacturers: Fluid Chillers Australia, PowerPax, Aquacoolers, Matsu
Note on A12: Applications: Portable/temporary form of air conditioning, main types include: Inexpensive portable for small spaces such as bed-rooms, small living areas (up to 4 kW) Industrial units designed for spot cooling in industrial plants, server rooms, hospitals and offices especially where electrical equipment creates a heat load Currently no MEPS requirements Key Equipment Suppliers/Brands: Mistral De Longhi Dimplex Electrolux Kelvinator Arlec Sanyo/Cara Denso/Australian Air Filters
Note on A13: Applications: These applications are design-critical (temperature/humidity) and downtime-critical air conditioning applications including systems for super computers, IT rooms, data cabinets, containers/shelters, pharmaceutical, medical and sensitive manufacturing applications. Key Equipment Suppliers Liebert - Market Leader Stulz Uniflair Air Design (RC Group) American Power Corp
Note on A16: Application: Heat pumps offer an energy efficient way to heat/cool swimming pools as they use renewable heat sources, such as air and water. They transfer heat from low-grade temperature sources and use a minimal amount of electricity to upgrade temperature to provide swimming pool heating. See http://www.enviro-friendly.com/quantum-solar-pool-heater.shtml Equipment suppliers include: Thermoswim Pooltherm Pacific Heat Pumps Local Manufacturers Accent Water & Energy Quantum APAC/Carrier QIM Aspen Toysei
Note on B1: kW relates to nominal cooling capacity (ARI 26.1oC db/19.4oC wb air on & 35oC ambient)
Note on C1: Raw data, need to take participation rate into account to estimate Quantity sold p.a.
Note on C3: Annual Sales data cross checked with 63,000 A/C compressors sold p.a. in Aust in 2006 by market leader Split System Applications = 148,217 p.a. x 0.3 locally manf. x 1 per unit x 0.95 market share= 42,242 RT Packages Applications = 5,194 p.a. x 0.6 locally manf. x 3 per unit x 0.7 market share = 6,544 Spares = 0.12 x 63,000 = 7,560 Swimming Pool HP = 900 x 0.95 = 855 Other Manufactured Applications = 5,799 = less than 10% Confirms annual data for Split Systems & RT Packages is correct order of magnitude & study has not overlooked more than 10% of miscellaneous applications using A/C compressors
Note on C5: DEH Import Data: Split Systems (incl. split, VRV & wall mounted split). 2005 = 730,858 2006 = 816,373 ABS Import Data: Split Systems (incl. split, VRV, wall mounted split & window). 2005 = 1,013,727 2006 = 1,061,758 2006 Industry Data (imported est.): Split Systems = 103,752 VRV = 3,000 Wall Hung Split Systems = 874,000 p.a. Total = 980,752 p.a. (WHS Systems Sold 655,500 reported Informark 2006) This difference of 207,137 p.a. between imports & sales is due to the depletion of inventory; industry run out of stock @ end of 2006
Note on C6: DEH Import Data 2006 = 166,807 2005 = 147,987
Note on C8: Require raw data to confirm annual sales & existing stock.
Note on C12: ABS Import Data 2005 = 25,188 2006 = 70,778 Estimate Existing Stock 7 x 30,000 = 210,000
Note on E1: Av. value is at wholesale (equipment only, not installed, excl. GST) add 20 to 30% GM for retail.
Note on F3: Residential Sales, Design & Admin = 8 hrs Ductwork = 2 x 6 hrs = 12 hrs Refrigeration = 1 x 5 hrs Electrical = 1 x (4 to 8) hrs (Depending on controls/zones) Commission, Handover & Call Back = 1 x 4 hrs Total = 35 hrs Estimate of Range of Av. installation for residential & light commercial applications is between 30 & 60 hrs.
Note on F5: Residential Sales, Design & Admin = 3 hrs Refrigeration = 1 x 5 hrs Electrical = 1 x 3 hrs Commission, Handover & Call Back = 1 hrs Total = 12 hrs Estimate of Range of Av. installation for residential & light commercial applications is between 10 & 20 hrs.
Note on F6: Residential (Window) Sales, Design & Admin = 2 hrs Installation = 1 x 4 hrs Total = 6 hrs Estimate of Range of Av. installation for residential & light commercial applications is between 6 & 10 hrs.
Note on F8: Residential Sales, Design & Admin = 4 hrs Ductwork & Installation = 2 x 5 hrs = 12 hrs Electrical = 1 x 1.5 hrs Commission, Handover & Call Back = 0.5 hrs Total = 18 hrs
Note on F9: Residential Sales, Design & Admin = 6 hrs Ductwork = 2 x 5 hrs = 10 hrs Plumber = 1 x 5 hrs Electrical = 1 x 3 hrs Commission, Handover & Call Back = 1 x 2 hrs Total = 24 hrs
Note on G14: Equivalent to work force of 10,664 based on 38 hr week & 48 weeks
Note on H1: Commercial Value Wholesale Value p.a. is calculated by multiplying Av. Value (wholesale) x Quantity Sold (units) p.a. The true commercial value can be estimated by multiplying the Wholesale Value by 2 to 4 times (depending on technology & complexity of application) to take into account installation costs & margins. Eg 6.0 kW Wall Hung Split Systems = $1,050 x 2 = $2,100 plus GST fully installed Eg 15.0 kW Split ducted System $3,189 x 2.5 (or x 3.0) = $7,970 to $9570 plus GST fully installed More complex installations (incl. commercial) use higher multipliers. The average multiplier accross all residential & light commercial applications is 2.4
Note on H3: Residential Price for 15.0 kW Split System Av. Unit @ wholesale = $3,190 plus GST Duct, Fittings, Controls @ wholesale = $1,350 plus GST Labour, Duct = $600, Electrical = $550, Refrig. = $800, Compliance Cert. = $25 Labour = $1,975 plus GST Material Cost = $4,540 plus GST Total Price (incl. 20% to 30% Gross Margin) = $8,145 to $9,310 plus GST Estimate of Range of Av. installation for residential & light commercial applications vary significantly from $8,000 upward depending on complexity of installation. Have nominated av. as $9,600 incl. GST, however would useful exercise to obtain quotations as prices vary significantly from State to State.
Note on H5: Retail Prices for 6.0 kW WHS System (incl. GST) Unit @ wholesale = $650 to $1585, Av = $1,150 Mark Up = $300 to $600 Installation = $650 to $1200 (Industry benchmark for Certified Back to Back is $750) Total = $1,150 + $450 + $800 = $2,350/1.1 = $2,140 (excl. GST)
Note on H6: Retail Prices for 3.5 kW (Window Unit) Unit @ wholesale = $450 plus GST Mark Up = $400 incl. GST Installation = $500 to $1000 incl. GST Total = $450 + $360 + $600 = $1,410 (excl. GST)
Note on H8: Consumer Price for 14.0 kW Evaporative Cooler Estimate Av. installation = $3,600 plus GST, however would useful exercise to obtain quotations as prices vary significantly from State to State & b/n brands.
Note on H9: Consumer Prices for 20 to 26 kW Gas Ducted Heater Estimate Av. installation = $3,200 plus GST, however would useful exercise to obtain quotations as prices vary significantly b/n brands & dealers.
Note on H12: Retail prices range from $650 to $1,400 incl. GST Av. price excl. GST = $775 Consumer pick-up or delivered, no installation required.
Note on I1: Participation rate is % of market incumbents participating in collection of raw data.
Note on J8: Require raw data to confirm annual sales & existing stock.
Note on J12: ABS Import Data 2005 = 25,188 2006 = 70,778 Estimate Existing Stock 7 x 30,000 = 210,000
Note on L10: DEH Import Data 2005 = 1,291 2006 = 499 Av. = 895 Total all Chiller Types Sold 2005/6 p.a. = 1,495
Note on M1: Status of AC in Australia, EES, 2005 pp12 Studies undertaken by Test Research in 1995 indicate the av. age of AC's to be 8 years, with the av, retirement age of 12 to 18 years (depending on installation, type), which was broadly consistent with BIS Shrapnel Data collected in 2004. The estimated life were based on discussions with Industy Product Managers, however broadly fall into categories indicated in studies.
Note on N3: Sread of product by state is as follows based on current data obtained from Industry: NSW&ACT = 36% Qld = 23% Vic = 13% WA = 13% SA = 12% Tas = 2% NT = 1%
Note on N4: VRV has only been available in Australia in recent years, estimated existing stock over 7 years
Note on N5: Sread of product by state is as follows based on current data obtained from Industry: Qld = 32% NSW&ACT = 27% Vic = 20% WA = 10.5% SA = 6.5% Tas = 2% NT = 2%
Note on N6: Regional split for window units is similar to Wall Hung Split Systems Existing installed stock is likely to be greater, however operation time is very low
Note on N7: Sread of product by state is as follows based on current data obtained from Industry: Vic = 32% Qld = 23% NSW&ACT = 22% WA = 12% SA = 8% NT = 2% Tas = 1%
Note on N8: EES National Share of A/C Type Estimates Evaps @ 20% of 7.7M households (incl. portable evaps). If we assume 50% of these are portable evaps, approx. existing stock = 770,000
Note on N13: Confirmed by Market Leader
Note on N16: On hold until Swimming Pool report/survey complete
This data was collected via extensive interviews with industry sources and used in conjunction with import data from DEWR, import statistics from ABS and some earlier estimates of installed devices from a variety of studies.
There is still a degree of conflict between import data and sales in some classes of equipment which is likely to be as a result of the drawdown of inventories. It is widely reported for instance that towards the end of 2006 suppliers had close to exhausted all stocks in inventory.
Numbers in blue are still under investigation or further data is coming that may change the value presently recorded.
The industry gain accurate information as follows:
- Market leaders with a significant share & years of experience have a good understanding of market sizes/details by product category
- Unit volumes & typical sizes are estimated at industry gatherings such as MEPS committees
- Several product categories are recorded by Informark, this information is only available to members that subscribe,
participants can estimate total market data by estimating participation rate.

## AC per Household
Ownership (Ratio of Existing Stockto the # Households)
Number of Households (000's) | Qld | NSW & ACT | Vic | Tas | NT | SA | WA | Aust
Family households: 2003 | 1465.7 | 2648.9 | 1880.4 | 194.2 | 55.3 | 627.2 | 768.5 | 7640.2
Projected Family Households, 2006 | 1583.1 | 2773.3 | 1975.6 | 202.8 | 67.2 | 649 | 806.3 | 8057.3
Projected Family Households, 2007 | 1620.3 | 2811.6 | 2003.7 | 204.5 | 68.4 | 654.9 | 822.4 | 8185.8
WHS System | 751074 | 696360 | 494913 | 44766 | 49740 | 159168 | 290979 | 2487000
Window/Wall Units | 539734.4 | 500416 | 355652.8 | 32169.6 | 35744 | 114380.8 | 209102.4 | 1787200
Portable | 63428.6844 | 58774.8461 | 41866.4244 | 3741.0321 | 4327.8646 | 13362.934 | 24488.258 | 209990.0436
Split System | 94843.7122 | 149481.6973 | 56182.7848 | 8565.9539 | 5588.9175 | 48417.9974 | 55918.9369 | 419000
Sub Total AC all Types (excl. Evap.) | 1449080.7966 | 1405032.5433 | 948615.0093 | 89242.586 | 95400.7821 | 335329.7313 | 580488.5949 | 4903190.0436
Evaporative Coolers | 217362.1195 | 210754.8815 | 142292.2514 | 13386.3879 | 14310.1173 | 50299.4597 | 87073.2892 | 735478.5065
Total AC all Types | 1666442.9161 | 1615787.4249 | 1090907.2606 | 102628.9739 | 109710.8994 | 385629.191 | 667561.8841 | 5638668.5501
Air Cond. Units per Household 2006 | 1.0526 | 0.58262 | 0.55219 | 0.50606 | 1.6326 | 0.59419 | 0.82793 | 0.69982
Note on A1: Ownership can exceed 1.0
Note on A2: Sources: ABS4442.0 Family Characteristics - June 2003 ABS3236.0 Household & Family Projections - 2001 to 2026
Note on A11: Have applied 15% of all AC types to estimate Evap Coolers (excl. portable). This estimate is a significant weakness in this analysis. Further data is required to qualify Existing Stock & correct distribution by state. Evap. Coolers are popular in WA, SA & rural NSW/Qld/Vic where humidity is low. Distribution by state is very different to other AC types.
There are several factors that effect the Ownership Ratio Calculation:
- Existing Stock Calculations & assumptions
- Proportion of WHS Systems, Split Systems & Window Wall units assigned to Residential & Commercial (see sensitivity analysis below)
- Weakness in the Evaporative Cooler data
Existing Stock Calculations & assumptions:
Assumed 100% of systems imported or manufactured were in service for the nominal warranty period (for domestic applications) then discounted the % in service to a typical life span. Existing Stock is calculated on AC Calculation WSheet, summary of assumptions used for calculations was as follows:-
Split Systems (Warranty period: majors = 5 yrs/minors = 3 yrs, used 4 yrs), then discounted to 70% at 10 years & 60% at 12 years)
WHS Systems (Warranty period: majors = 5 yrs/minors = 3 yrs, used 4 yrs), then discounted to 60% at 10 years
Window/Wall (Warranty period: 3 yrs), then discounted to 65% at 10 years & 55% at 12 years)
Evaporative Coolers (Warranty period: 3 yrs), then discounted to 70% at 10 years & 60% at 12 years)
Existing Stock can be subjective as units can still be installed, however not operated or only used occasionally (a good example of this is a wall unit replaced by a WHS System, wall units are rarely replaced in a domestic application as it involves re-plastering & filling the external hole at a cost of $500 to $1,000).
There is limited research in this area, however one reference is as follows:
Status of AC in Australia, EES, 2005 pp12 Studies undertaken by Test Research in 1995 indicate the av. age of AC's to be 8 years, with the av, retirement age of 12 to 18 years (depending on installation, type), which was broadly consistent with BIS Shrapnel Data collected in 2004. Until a more comprehensive study is undertaken intuition from industry Product Managers & Service Managers is the best guide.
Proportion of WHS Systems, Split Systems & Window Wall units assigned to Residential & Commercial
Highly recommend a survey of major suppliers (incl. Daikin, Fujitsu, Mitsubishi, Carrier, etc.) to obtain a better understanding of the % of Commercial AC to domestic applications. The major players will have an indication of this split as they offer different warranties & have different departments for residential & commercial.
The estimated ratios were as as follows:
WHS Systems = 25%, Window/Wall Units = 20% & Split Systems = 50% Commercial alters the "macro data".
Av. Devices per Household of 0.70, Total Energy Consumed for Commercial = 17,654 GWh/a & Residential = 5,248 GWh/a
Amending the ratios to WHS Systems = 20%, Window/Wall Units = 15% & Split Systems = 40% Commercial
Av. Devices per Household of 0.75, Total Energy Consumed for Commercial = 15,878 GWh/a & Residential = 5,755 GWh/a
Amending the ratios to WHS Systems = 30%, Window/Wall Units = 25% & Split Systems = 50% Commercial alters the "macro data".
Av. Devices per Household of 0.66, Total Energy Consumed for Commercial = 18,414 GWh/a & Residential = 4,989 GWh/a
Weakness in the Evaporative Cooler data
Have applied 15% of all AC types to estimate Evap Coolers (excl. portable). This estimate is a significant weakness in this analysis. Further data is required to qualify Existing Stock & correct distribution by state. Evap. Coolers are popular in WA, SA & rural NSW/Qld/Vic where humidity is low. Distribution by state is very different to other AC types. The ownership ratio would increase if we were to include portable evaporative coolers in the analysis (have excluded them in this analysis as they are inexpensive, consume very little power & in some cases provide marginally better cooling than a pedestal fan).

## AC Refrigerant Stock
Split Systems
Brand | Model | Nom. Cooling Capacity (kW) | Type (Reverse Cycle) |  | Refrig. Type | Pre-Charge (g) | Pre-Charge Length (m) | Additional Charge (g/m) | Max Pipe Run (m) Length/Height
Hitachi | RAS-6H | 16 | Split System | Inverter | R410A | 3800 | 30 | 110 | -
Hitachi | RAS-140 | 15.3 | Split System | Const Spd | R407C | 4700 | 7.5 | - | -
Lennox | HP29-048 | 14.1 | Split System | Const Spd | R22 | 4050 | 4.6 | - | -
Daikin | RY140LUY1 | 14.5 | Split System | Const Spd | R22 | 4100 | 30 | - | 50/30
Daikin | RMXS140 & 160 | 14.0 & 15.5 | Split System | Inverter - Multi | R410A | 5100 | 0 | - | -
Mitsubishi Electric | - | 15.2 | Split System | Const Spd | R22 | 5000 | 30 | - | -
Refrigerant Type | Refrig. Ratio | Av.Charge per Installed System | Tons of Refrig
R22 | 80% | 4.7 | 3150.88
R407C | 5% | 5.5 | 230.45
R410A | 15% | 4.7 | 590.79
Existing Stock = | 838000
Assume ratio of installed base of refrigerants R22: R407C: R410 = 80:5:15
Assume av. pipe length = 15m
Average nominal cooling capacity of 15.0 kW
WHS Systems
Brand | Model | Nom. Cooling Capacity (kW) | Type (Reverse Cycle) |  | Refrig. Type | Pre-Charge (g) | Pre-Charge Length (m) | Additional Charge (g/m) | Max Pipe Run (m) Length/Height
Lennox | LNC050C2 | 5 | WHS System | Const Spd | R22 | 1740 | 5 | 30 | 10
Lennox | LNC062C2 | 6.2 | WHS System | Const Spd | R22 | 1930 | 5 | 30 | 10
Hitachi | RAS51CHA3 | 5.1 | WHS System | Const Spd | R22 | 1400 | 8 | 25 | 15/5
Hitachi | RAS63CHA4 | 6.3 | WHS System | Const Spd | R22 | 1650 | 8 | 20 | 15/5
Daikin | RY50GA | 5.2 | WHS System | Const Spd | R22 | 1550 | 10 | - | 30/15
Daikin | RY60GA | 6.2 | WHS System | Const Spd | R22 | 1750 | 5 | - | 30/15
[5 empty] | Av. | 1670
Lennox | LNE047V1 | 4.7 | WHS System | Inverter | R410A | 1170 | 5 | 30 | 10
Hitachi | RAS50YHA | 5 | WHS System | Inverter | R410A | 1400 | 20 | 0 | 20/10
Hitachi | RAS60YHA | 6 | WHS System | Inverter | R410A | 1420 | 20 | 5 | 30/10
Mitsubishi | MSZ-A18YV | 5 | WHS System | Inverter | R410A | 1800 | 7 | 20 | 30/15
Mitsubishi | MSZ-A24YV | 6 | WHS System | Inverter | R410A | 1800 | 7 | 20 | 30/15
Daikin | FTKSXS50 | 5 | WHS System | Inverter | R410A | 1500 | 10 | 20 | 30/20
Daikin | FTKSXS60 | 6 | WHS System | Inverter | R410A | 1500 | 10 | 20 | 30/20
[5 empty] | Av. | 1512.8571
Refrigerant Type | Refrig. Ratio | Av.Charge per Installed System | Tons of Refrig
R22 | 75% | 1.7 | 4227.9
R410A | 25% | 1.5 | 1243.5
Existing Stock = | 3316000
Assume ratio of installed base of refrigerants R22: R410A = 75:25
Assume av. pipe length = 5m
Average nominal cooling capacity of 5.9 kW
Window/Wall & Portable
Brand | Model | Nom. Cooling Capacity (kW) | Type (Reverse Cycle) | Refrig. Type | Pre-Charge (g)
Lennox | LNC0503702201 | 3.7 | Window | R22 | 980
Lennox | LNC0504802201 | 4.8 | Window | R22 | 1400
Mitsubishi Electric | MWH12KV | 3.5 | Window | R22 | 900
Electrolux | EWJ18CRA | 5.3 | Window | R22 | 1000
LG | LWG050AC-6 | 1.73 | Window | R22 | 300
LG | LWC122RC-6 | 3.52 | Window | R22 | 520
LG | LWM185RC-6 | 4.5 | Window | R22 | 780
|  |  |  | Av. | 840
Refrigerant Type | Type (Reverse Cycle) | Refrig. Ratio | Av.Charge per Installed System | Tons of Refrig
R22 | Window | 100% | 0.84 | 1876.56
R410A | Window | 0% | - | -
R22 | Portable | 70% | 0.5 | 73.5
R410A | Portable | 30% | 0.5 | 31.5
Existing Stock (Window/Wall) = | 2234000
Existing Stock (Portable) = | 210000
Note on A16: Refrigerant Use Trends: Split Systems R22 was the preferred choice of refrigerant for both local & overseas manufacturers on constant speed units over the last 10 to 15 years. The introduction of inverter technology saw R410A used on single phase units up to 15 kW (some suppliers offering larger models). Constant speed models (single phase & three phase) are migrating towards R407C & R410A.
Note on A42: Refrigerant Use Trends: Split Systems R22 was the preferred choice of refrigerant throughout the 1990's & early 2000's. The introduction of inverter technology, higher efficiency requirements & greater environmental awareness has driven a swing towards R410A models to the extent were some major suppliers (ie Mitsubishi Electric) no longer offer R22 models. Despite the recent dominance of new R410A models, the installed base would still be dominated by R22 models.
Note on A57: Refrigerant Use Trends: Window/Wall & Portable R22 was the preferred choice of refrigerant for both local & overseas manufacturers on Window/Wall Units over the last 10 to 15 years. Due to recent MEPS changes a handful of manufacturers have justified the expenditure of migrated to R410A, however many are still on R22. Portable units are slightly different, where R22 was the dominate choice of refrigerant, however models such as the Electrolux EPV09CRA & EPV12CRA were developed for the European market (use R410A/240V) & drive more R410A units into the portable installed base.
Note on C11: Av. of Daikin & Lennox = (4.1 + (4.05 + 10.4 x 0.11))/2 = 4.647 kg
Note on C12: = 4.7 + (7.5 x 0.11) = 5.525 kg
Note on C13: Av. of Hitachi & Daikin = (3.8 + 5.67)/2 = 4.735 kg
Note on C38: Av. of sample of 6 off R22 models ranging from 5.0 to 6.3 kW
Note on C39: Av. of sample of 7 off R410A models ranging from 4.7 to 6.0 kW
Note on D58: Av. of sample of 7 off R22 models ranging from 1.73 to 4.8 kW
Note on I7: Chargeless Piping Length = 0 m Additional Additional Charge = Total length (m) of liquid pipe dia 9.5 x 0.054 + Total length (m) of liquid pipe dia 6.4 x 0.022 Eg: 7.5m of ea. = Additional 0.57 kg Total Charge = 5.1 + 0.57 = 5.67 kg

## Chillers
Chiller Applications | Nominal Size
Commercial Air Conditioning | Med/Large
Process Chilling (Food Chain)
Dairy Industry | Small/Med
Milk Harvesting and Storage | Small/Med
Milk Processing | Small/Med
Cream Cheese Industry | Small/Med
Horticultual Products | Small/Med
Fruit & Veg | Small/Med
Brewing and Winemaking | Small/Med/Large
Food processing (Confectionary, Frozen Foods, | Small/Med
Drinks, Fruit Juice, Chilled Water as additive) | Small/Med
Abattiors & Meat Processors (inc. pig & poultry) | Large
Aqua Culture & Seafood | Small/Med
Ice Making (small) | Small
Industrial Applications
Plastics/die cooling | Small
Electronic Plating | Small
Printing machines & associated equipment | Small
Dry Cleaning | Small
Pharmaceutical/CSL | Lots of little plants
Co-generation | Small/Med
Laser cutting equipment | Small
Construction | Rare
Cooling of water for industrial processes | -
Other Applications
Mining and Tunnels | Large & Small
Petro-chemical/Gas & Chemical | Large & Small
Cooling water for medical or chemical equipment such as SEM, MRI and X-Ray units | Small
Liquifaction and Cryogenics | Small
Estimated Australian Market Size 2005/06
Annual # Chillers Imported/Manufactured
Capacity |  | W.C. | A.C. | Total # of Chillers
KwR |  | # units | # units | # units
< 110 | Small | 19 | 356 | 375
>110-350 | Medium | 27 | 248 | 275
>350-528 |  | 60 | 240 | 300
> 528-700 | Large | 50 | 175 | 225
>700-1055 |  | 65 | 55 | 120
>1055-1750 |  | 92 | 10 | 102
>1750-3517 |  | 35 | 0 | 35
>3517-7034 |  | 6 | 0 | 6
Total |  | 354 | 1084 | 1438
Disection of Chillers by Size/Applications
Small: 50% Food Chain, 50% Industrial/Other |  | # units | Av. kW | Weighted Av.
< 110 |  | 375 | 60 | 22500
60
Medium: 33.3%ea. Comm. AC, Food Chain, Industrial/Other |  | # units | Av. kW | Weighted Av.
>110-350 |  | 275 | 230 | 63250
>350-528 |  | 300 | 439 | 131700
|  | 575 | - | 194950
339.0435
Large: 85% Commercial AC & 7.5% Food, 7.5% Ind/Other |  | # units | Av. kW | Weighted Av.
> 528-700 |  | 225 | 614 | 138150
>700-1055 |  | 120 | 878 | 105360
>1055-1750 |  | 102 | 1402 | 143004
>1750-3517 |  | 35 | 2634 | 92190
>3517-7034 |  | 6 | 5276 | 31656
|  | 488 | - | 510360
1045.8197
| # units | Av. kW | Weighted Av. | Est. Av. Life (Yrs) | Existing Stock
Food Chain: Small | 187.5 | 60 | 11250 | 15 | 2800
Food Chain: Medium | 191.6667 | 339 | 64975 | 20 | 2900
Food Chain: Large | 36.6 | 1046 | 38283.6 | 25 | 600
| 415.7667 |  | 275.4155 |  | 6300
Industrial & Other: Small | 187.5 | 60 | 11250 | 15 | 2800
Industrial & Other: Med | 191.6667 | 339 | 64975 | 20 | 2900
Industrial & Other: Large | 36.6 | 1046 | 38283.6 | 25 | 600
| 415.7667 |  | 275.4155 |  | 6300
Comm. AC: Med | 191.6667 | 339 |  | 20 | 2900
Comm. AC: Large | 414.8 | 1046 |  | 25 | 6950
| 606.4667 |  |  |  | 9850
Total Installed Chillers |  |  |  |  | 22450
Energy Calculations: Chillers
Australia
Chillers: Food Chain
Effective Operating Hrs/day | 8
Existing Stock | 6300
Total Running Hrs/a | 18396000
Food Chain kWh/a | 1688848076.3249
Chillers: Industrial App & Other
Effective Operating Hrs/day | 10
Existing Stock | 6300
Total Running Hrs/a | 22995000
Industrial App & Other kWh/a | 2111060095.4061
Assumptions for Sensitivity Analyisis
| Food Chain | Industrial & Other
COP | 3 | 3
Av. Capacity kW | 275.4155 | 275.4155
Existing Stock | 6300 | 6300
Effective Run Time | 8 | 10
Note on A3: There are approx. 8,000 registered water cooling towers in Victoria (25% of population). National installed base of chillers is approx. 32,000. Can be two or more water towers per chiller & water towers are not just used for Air Conditioning.
Note on B99: Less than Industrial due to seasonality
Chiller Analysis & Assumptions:
The following process was undertaken in conjunction with discussions with industry (Manufacturers & Contractors):
1. Chillers were broken into 3 categories by capacity (Small <110kW; Medium between 110 & 528kW; Large >528kW)
2. Chillers were placed into 3 Market sectors (Commercial AC; Process Chilling in Food Chain; Industrial & Other applications)
3.Chiller Applications were classified as large, medium & small & an estimate made of Market segment share in each size (eg Large consisted of 85% Commercial AC & balance shared) or (eg Small consisted of 50% Process Chilling in Food Chain & 50% Industrial/Other)
4. Annual volumes, weighted averages, average sizes, estimated existing base & energy consumptions are calculated below. An assumption table is provided below listing COPs, existing stock & effective run time (which is subjective & requires further investigation).
Total Estimated Energy Consumed by Chillers:
Commercial Air Conditioning = 4,857 GWh/a
Process Chilling (Food Chain) = 564 GWh/a
Industrial Applications & Other = 705 GWh/a
Other useful references
MEPS - Commercial Building Air Conditioning Chillers (Vapour Compression), 2004.
pp 5 Estimated that there are some 6,000 to 7,000 chillers of varying technology
types, efficiencies and refrigerants currently installed in Australian commercial buildings,
entertainment complexes and retails facilities.
pp 6 Figure 1 shows the range of sales by type of chiller. Applications with cooling requirements below 250 kW are mainly dominated by scroll compressors, with other applications up to 1,000 kW using a mixture of helical rotary (screw) and reciprocating compressors. Cooling capacity requirements above 1,000 kW is usually managed by the use of screw and centrifugal compressors.

## Cold Food Chain
Refrigerated Cold Food Chain
Applications
Dairy Farmers | Trucks | Dairy Industry | Trucks | Large Cold Stores | Trucks | Supermarkets | Household
Fruit Farmers | Light Com | Beverages | Light Com | Chiller = 3oC | Light Com | Convenience Stores | Restaurants
Vegetable Farmers | Trains | Frozen Foods | Trains | Freezer = -20oC | Trains | Pubs, Clubs & Rest | Hotels
Livestock Producers | Air | Abattoirs & Meat Processors | Air | 7.5 Million m3 | Air | Takeaway Foods | Hospitals
Poultry Farmers | Marine | Poultry Processors | Marine | 50% Chillers | Marine | Vending Machines
Aquaculture |  | Confectionary |  | 50% Freezers |  | 80 to 85% Med Temp
Refrigeration Technology
Chillers | Refrig: | Industrial Refrigeration | Refrig: | Cold Storage | Refrig: | Supermarket Systems | Household Refrig. Appliances
Icemakers | Truck:Trailer/Inter-modal | Chillers | Truck:Trailer/Inter-modal | Cool Rooms | Truck:Trailer/Inter-modal | Cool Rooms | Commercial Ref/Freezer
Industrial Refrig. | Truck: Rigid | Freezers | Truck: Rigid |  | Truck: Rigid | Display Cases | Merchandising Equipment
Cold Rooms | Powered Off-Vehicle | Icemakers | Powered Off-Vehicle |  | Powered Off-Vehicle | Reach in Refrigerators
| Containers | Cold Storage | Containers |  | Containers | Reach in Freezers
|  | Cool Rooms |  |  |  | Vending Machines
Ice Cream Displays
Ice Making Equipment
Ammonia/R22/R507C/R404A | R134a | Ammonia/R22/R507C/R404A | R134a | Ammonia/R22/R507C | R134a | R22/R404A/R507/CO2/R134a | R134a/R404A/HC
Chillers = 327 GWh/a | Trans. = Mt CO2 -e | Chillers = 237 GWh/a | Trans. = Mt CO2 -e | Industrial Refrig. = 356 GWh/a | Trans. = Mt CO2 -e | Supermarket = 5,270 GWh/a | Household = 8,330 GWh/a
Industrial = 206 GWh/a |  | Industrial = 150 GWh/a |  |  |  | Cool Room = 100 GWh/a | Cool Room = 47 GWh/a
Pubs/Clubs/Convenience Stores/Take Away Food
Cool Rooms = 118 GWh/a |  | Cool Rooms = 51 GWh/a |  | Cool Rooms = 106 GWh/a |  | Merchandising = 2,620 GWh/a
Total = 455 to 651 GWh/a |  | Total = 326 to 438 GWh/a |  | Total = 462 to 605 GWh/a |  | Total = 8,480 to 9,156 GWh/a |  | 9,470 GWh/a
Total Energy Consumption Estimated at 19 to 20,000 GWh/a
Types of Businesses Supplying/Installing/Servicing Refrigeration Technology
Refrigeration Mechanics employed by Small/Medium/Large Contractors, Super Market Contractors, Industry,
Refrigerated Transport Coys, Appliance Manufacturers/Suppliers
Wholesalers of Refrigeration Equipment, Components, Cu Pipe, Controls, Tools & Accessories
Suppliers of Refrigeration Equipment, Components, Cu Pipe, Controls, Tools & Accessories
Cool Room manufacturers/contractors
Note on A24: Allocation of Chiller & Industrial Energy Consumption between primary & secondary processing is 58:42 split CSIRO overall split between primary & secondary was 58%: 42%, however believe secondary energy consumption has been under estimated. Further investigation required with suppliers/contractors chillers/industrial refrigeration.
Note on A29: CSIRO estimate = 455 GWh/a ES estimate = 651 GWh/a
Note on D29: CSIRO estimate = 326 GWh/a ES estimate = 438 GWh/a
Note on G29: ES estimate = 462 GWh/a CSIRO estimate = 605 GWh/a
Note on J29: CSIRO estimate = 8,480 GWh/a, which was largely based on estimates in MEPS reports. Have confirmed that some of this data is understated.
Primary Producers
(Initial Cooling
Fresh Produce)
Refrig.
Trans
Retail Display &
Cold Room Storage
End User
Refrig.
Trans
Food Processors/Mfrs
(Secondary Chilling
& Freezing)
Refrig.
Trans
Cold Storage
Logistics & Distribution

## CC-Cold Storage
See Energy Calc. Estimate Below
Public Cold Storage Capacity |  |  | Swire Refrigerant Site Summary | [5 empty] | Case Studies
Company | Refrigerated Capacity Million m3 |  | Location/Site | State | Refrigerant | Refrigerated Capacity m3 | Estimated Tons
Swire | 2.022 |  | Clayton | Vic | R22 | 139439 | 6
Oxford | 0.88 |  | Doveton | Vic | R22 | 115980 | 5
Versacold | 0.996 |  | Lyndhurst | Vic | Ammonia | 160449 | 4.5
Toll | 1.6 |  | Other Vic | Vic | Ammonia | 23132 | -
Montague | 0.25 |  | Homebush | NSW | R22 | 116779 | 5
Scots | 0.15 |  | Lurnea | NSW | R22 | 84432 | 4
Harbourside | 0.04 |  | Minto | NSW | R22 | 73219 | 3
Victoria Cold Storage | 0.04 |  | Other NSW | NSW | Ammonia | 126570 | 5
Lago Coldstores | 0.04 |  | New NSW | NSW | Ammonia | 90249 | 5
CB Cold Storage | 0.04 |  | Hemmant 1 | Qld | R22 | 149978 | 6
Doboy Coldstores | 0.06 |  | Hemmant 2 | Qld | Ammonia | 56634 | 2
Devonport | 0.08 |  | Hemmant 3 | Qld | Ammonia | 67246 | 2.5
Burnie Ports | 0.28 |  | Murarrie | Qld | Ammonia | 59087 | 2.5
Hobart | 0.13 |  | Cannon Hill | Qld | Ammonia | 209544 | 6
Others commercially available* | 0.96079 |  | Other Qld | Qld | - | 5511 | -
|  |  | Townsville | Qld | Ammonia | 8170 | 2
TOTAL | 7.5688 |  | Legana | Tas | R22/R504 | 18471 | 2
|  |  | Other Tas | Tas | - | 5529 | -
|  |  | Dry Creek, Cavan 1 | SA | Ammonia | 49721 | 2
|  |  | Cavan 2 | SA | Ammonia | 62966 | 2
|  |  | Cavan 3 | SA | Ammonia | 42012 | 2
|  |  | Mile End | SA | Ammonia | 40188 | 2
|  |  | Port Adelaide | SA | Ammonia | 42463 | 2
|  |  | Croydon | SA | Ammonia | 45000 | 2
|  |  | Banjup | WA | Ammonia | 159679 | 5
|  |  | Palmyra | WA | Ammonia | 66014 | 2.5
|  |  | Other NT | NT | - | 2800 | 1
|  |  | TOTAL |  |  | 2021262 | 81
Swire Cold Storeage Analysis
Location/Site | Refrigerant | m3 | kWh/day | kWh/a | Energy Bill | Check Cost/kWh | kWhr/a per m3 | Refrig. Only
Clayton | R22 | 139439 | 17647 | 6441155 | 368000 | 0.057133 | 46.1934 | 39.2644
Lyndhurst | Ammonia | 160449 | 16735 | 6108275 | 329000 | 0.053861 | 38.0699 | 32.3594
Industry Calculation
| Based on Swire Actuals GWh/a | Av. CSIRO & Actual GWh/a
Ammonia | 227.04 | 319.275
R22 | 92.235 | 605
| 319.275 | 462.1375
|  | Estimated Energy Consumed Cold Storage (Channel) GWh/a = | 462.1375
Assumptions:
Ammonia/R22 | 75/25
Chiller/Freezer | 50/50
Total Million m3 | 9.46
Ammonia: kWhs/pa per m3 | 32
R22: kWhs/pa per m3 | 39
% Energy Consumed by Ref. | 85%
Note on A3: Capacities estimated by Dr Silvia Estrado-Flores from CSIRO Food Futures, November 2006
Note on A7: Swires, Oxford, Versacold and Toll own about 70% of the national total.
Note on A18: Estimated as 15% of the sub-total of all the known refrigerated capacities.
Note on B20: Ratio of Freezers (low temp) to Chillers (medium temp) The ratio of Freezers to Chillers is different in Cold Storage to the rest of the food chain. This difference in ratios may be explained as follows: In retail, storage & turn-over is driven by demand & economics, GMROI (Gross Margin Return on Inventory). A proven industry ratio (based on forecasts of compressors/condensing units) in Commercial refrigeration is 20% low temp & 80% medium temp. This is similar to the ratio of freezers to refrigerated space in domestic refrigeration (pp 12 CSIRO). In Cold Storage the ratio is not as clear cut as facilities are often designed to do both & switch depending on clients' needs. On pp 10, CSIRO make reference to a USDA study 2006 that shows cold store use is generally 50% freezer and 50% refrigerated. Goods stored in chillers generally have a have a shorter shelf life & turn-over in weeks. Whereas goods in freezers have longer shelf lifes & turn-over every 2 to 3 months. Manufacturers take advantage of the longer shelf life which results in a higher ratio of freezer to chiller than seen in commercial refrigeration, retail or households.
Note on D3: Data derived from different sources: - - Sites/refrigerants based on Swire document dated Aug 2004 - Initial m3 capacities based info on www.rwta.com.au/ - Other Vic/Qld/etc updated from www.swirecoldstorage.com.au - New NSW sites from CSIRO study - Accuracy could be improved via phone calls to regional Swire engineers.
Note on G35: Swire Energy cost is very low, probably below cost of production and distribution, however such a low price is not uncommon, a major Supermarket chain currently pays 3.5 to 4c per kWh.
Case Study
Swire's Lyndhurst, Victoria
Refrigerated Storage = 160,449m3
Floor area = 18,890m2 (Av. height = 8.5m)
Pallets = 16,000, conventional storage (manual)
No direct employees on site = 240 over 3 shifts
Age = 6 years
Refrigerant = 4 to 5 tons of Ammonia
Type = Chiller 75% & Freezer 25%
Refrigeration system design:
Compound compressor, single motor driving 2 compressors
 Low temp: 616kW x 2 @ -20oC, estimated heat load of 713kW
 High temp: 916kW x 1 @ 2 to 4oC, estimated heat load of 574kW
 Operating @ 816kW today with peak setting of 900kW
Energy consumption = 16,735kWhrs/Day, operates 24/7, 365 days
Estimate 85% of energy consumption is for refrigeration
Maintenance = system only down for 4 hours, operates 99.5% of time
Refrigerant top up = 65kg cylinder every 3 years, 0.5% p.a.
Energy Bill = $329,000p.a. x 0.85 = $280,000p.a. on refrigeration
Case Study
Swire's Clayton, Victoria
Refrigerated Storage = 139,439m3
Floor area = 10,728m2 (Av. height = 13.0m)
Pallets = 22,000, non conventional (automated, cranes)
No direct employees on site = 30 to 40 over 2 shifts
Refrigerant = Approx. 6 tons of R22
Type = Chiller 12% & Freezer 88%
Refrigeration system design:
 3 individual screw compressors
 Available cooling: 1616, Av. operating: 1200/700kW (summer/winter)
Energy consumption = 17,647kWhrs/Day, operates 24/7, 365 days
Estimate 85% of energy consumption is for refrigeration
Maintenance = system only down for 4 hours, operates 99.5% of time
Refrigerant top up = 65kg cylinder every 1 year, 1% p.a.
Energy Bill = $368,000p.a. x 0.85 = $313,000p.a. on refrigeration
*Silvia Estrado-Flores from CSIRO Food Futures, November 2006
IIR estimates refrigeration to account for 85% to 90% of total running expense, Swire study confirmed at 85%.
IARW, 2006 estimate 30% of storage facilities in the US are private, CSIRO assumed a conservative percentage of 20%.
Total Australian cold storage capacity = 7.568 / 0.8 = 9.46 Million m3
Silvia Estrado-Flores from CSIRO Food Futures, November 2006 used two methods then an average of two methods) to estimate the Energy Consumption for Cold Storage, however the key difference between Swire actual & CSIRO estimate is the kWh/m3 rate.
CSIRO used 72kWh/m3 based on the average of 3 values sited in reports across NZ & UK. Based on interviews with Swire engineers, Swire actual was 32 to 39kWh/m3.

## CC-Supermarket
Retail: Supermarket
Method 1: Supermarket Specification
Segment | % Energy Consumed | GWh/a |  | Size | kW | # Stores | kW | kWh/a | Application | Run Hrs
Supermarket | 71.71% | 5270.4 |  | Supermarket: Lg | 350000 | 1200 | 420000000 | 2688000000 | Super Mkt | 16
Convenience Stores | 2.743% | 201.6 |  | Supermarket: Md | 230000 | 1500 | 345000000 | 2208000000 | Convenience Store | 16
Pubs & Clubs & Restaurants | 3.076% | 226.1 |  | Supermarket: Sm | 60000 | 975 | 58500000 | 374400000 | Pubs & Rest | 12
Take Away Food | 9.405% | 691.2 |  | Total | - | - | 823500000 | 5270400000 | Take Away | 12
Mech Cabinets & Vend machines | 13.06% | 960 |  |  |  | 3675 |  |  | Merch Cab | 16
Total | 100% | 7349.3
Method 2: MEPS, 2000
By Business Type: Method 2 | % Energy Consumed | GWh/a |  | Supermarket Analysis | GWh/a | Equipment Type | kWh/a
Supermarket: Lg | 32% | 1856 |  | Supermarket Total | 2378 | Central | 551893
Supermarket: Md | 8% | 464 |  |  |  | Display Case | 338257
Supermarket: Sm | 1% | 58 |  |  |  | Self Contained | 46850
Clubs: Lg | 9% | 522 |  |  |  | Total | 937000
Clubs: Sm | 2% | 116 |  | Check
Grocery Stores | 3% | 174 |  | Size | kWh/a | # Stores | kWh/a
Service Stations: Lg | 9% | 522 |  | Supermarket: Lg | 937000 | 1200 | 1124400000
Bottle Shops | 2% | 116 |  | Supermarket: Md | 615742.8571 | 1500 | 923614285.7143
Fresh Meat, Fish & Poultry | 6% | 348 |  | Supermarket: Sm | 160628.5714 | 975 | 156612857.1429
Pubs | 6% | 348 |  | Total | 1713371.4286 | - | 2204627142.8571
Café's Restaurants | 13% | 754
Other | 9% | 522
Total Remote: Comm Refrig. | 100% | 5800
Self-contained Display Cases
Glass Door Merchandisers
Reach in Refrigerators
Reach in Freezers
Ice Making Equipment
Refrigerated Vending Machines
Ice Cream Displays
Cold Water Dispensers
Total Self Contained: Comm Refrig. |  | 2680
Total Comm. Refrig. |  | 8480
Method 3: Actual Running Costs |  |  |  | Method 3 | Method 1
Size | kWh/a | # Stores |  | kWh/a | kWh/a
Supermarket: Lg | 1543972 | 1200 |  | 1852766400 | 2688000000
Supermarket: Md | 1014610 | 1500 |  | 1521915000 | 2208000000
Supermarket: Sm | 381118.4 | 975 |  | 371590440 | 374400000
Total |  | - |  | 3746271840 | 5270400000
Energy Bill: Super IGA (Yarram, Vic)
Month | kWh/Month | $/Month
2006-03-01 | 55047 | 6693
2006-04-01 | 45147 | 5605
2006-05-01 | 46242 | 5855
2006-06-01 | 45323 | 5005
2006-07-01 | 43401 | 5525
2006-08-01 | 46182 | 5187
2006-09-01 | 45814 | 5085
2006-10-01 | 48487 | 5360
2006-11-01 | 49405 | 5435
2006-12-01 | 52537 | 5607
2007-01-01 | 56100 | 6197
2007-02-01 | 52651 | 5775
| 586336 | 67329 | 0.11483
Assumptions
% Energy Consumed on Refrigeration = | 65%
Note on A2: Source: K Finn, Heatcraft, 2007 Cold Chain Specialist Calculation based on: - Refrigeration Capacity in Supermarket Specifications - Av. COP = 2.5 - Typical Running time = 16 hrs
Note on A11: Mark Ellis & Ass, 2000 MEPS for Remote Commercial Refrig.
Note on A25: Mark Ellis & Ass, 2000 MEPS for Remote Commercial Refrig. Total Energy Consumed = 4,380 GWh/yr in 2000, growing at 4.8% 2006 = 5,800 GWH/YR
Note on A34: Mark Ellis & Ass, 2000 MEPS for Self Contained Commercial Refrig. Total Energy Consumed = 2,200 GWh/a in 2000 Growth rate = 4.8%
Note on A35: Estimate used by CSIRO Based on Mark Ellis & Ass Reports
Note on D60: Includes all charges Energy, Network & Other
Information Provided by Energy Engineer of Major Supermarket Chain
"From submetering we have installed in a number of our stores; and based on the refrigeration component of a typical store of total consumption, we know that for an average sized store we consume approximately 1,200,000 to 1,300,000 kWh per annum."
This provides us with two equations:
Large = 350/250 x Medium
(Based on specifications provided by contractors on refrigeration requirements in Medium & Large stores)
Large x 1200/2700 + Medium x 1500/2700 = 1,250,000 kWh/a
(Assumed ratio of Major Supermarket chain providing information is indicative of rest of industry)
Therefore
Large Store = 1,543,972 kWh/a
Medium Store = 1,014,610 kWh/a
Energy Consumption Estimation
Three methods were undertaken
Method 1: Based on Supermarket Specifications provided by Contractors = 5,270 GWh/a
Method 2: Based on MEPS 2000 report adjusted to 2006 = 2,680 GWh/a
Method 3: Based on actual kWh/a in supermarkets = 3,746 GWh/a
Have adhered to result obtained in Method 1: despite actual data provided by major supermarket chain suggests an estimate of 3,746 GWh/a. The estimate was based on sub-metering in Target stores which can under estimate energy consumption of low efficiency stores. There are significant energy consumption differentiators including sub-coolers, floating head technology & studies on reconditioning stores have reported improvements up to 20%.
Further discussion is required with major supermarket chain or energy providers to qualify further.

## CC-Coolrooms
Cool Rooms | [13 empty] | Farm |  | Catering |  | Shop |  | Supermarket |  | Cold Storage (Channel)
Description | Application | From (m3) | To (m3) | From (m2) | To (m2) | Av. | W/m2 | Av. W | Nominal HP Cond. Unit | Technology | Cond. Units Sold p.a. | Installed Base | Most Common Refrig. Type | # Coolrooms | GWh/a | # Coolrooms | GWh/a | # Coolrooms | GWh/a | # Coolrooms | GWh/a | # Coolrooms | GWh/a | Total | GWh/a
Deli Case/Other Retail | Mechandising | - | - | - | - | - | - | 1000 | Fractional | Hermetic | 30269 | 181614 | R134a/R404A/R22 | na | - | - | - | - | - | - | - | na | - | 169134 | 395097024
Mini (up to 3m x 3m) | Coolroom | 0 | 21.6 | 0 | 9 | 9 | 250 | 2250 | Up to 1 | Hermetic |  |  | R134a/R404A/R22 | 3744 | 19678464 | 3120 | 16398720 | 4368 | 22958208 | 0 | 0 | 1248 | 6559488 | 12480 | 65594880
Small (up to 6m x 4m x 3m) | Coolroom | 22 | 72 | 9 | 24 | 16.5 | 250 | 4125 | 1 to 3 | Hermetic & Semi | 5134 | 41072 | R404A/R22 | 3136 | 30218496 | 1344 | 12950784 | 2240 | 21584640 | 1344 | 51803.136 | 896 | 8633856 | 8960 | 86338560
Medium (6m x 6m x 4m) | Coolroom | 73 | 144 | 24 | 36 | 30 | 300 | 9000 | 3 to 5.5 | Hermetic & Semi |  |  | R404A/R22 | 960 | 20183040 | 480 | 10091520 | 1440 | 30274560 | 1440 | 100915.2 | 480 | 10091520 | 4800 | 100915200
Large (10m x10m x 4m) | Coolroom | 145 | 400 | 36 | 100 | 68 | 300 | 20400 | 5.5 to 12.5 | Hermetic & Semi |  |  | R404A/R22 | 800 | 38123520 | 160 | 7624704 | 320 | 15249408 | 1280 | 203325.44 | 640 | 30498816 | 3200 | 152494080
Warehouse (20m x 10m x 4m) | Coolroom | 401 | 800 | 100 | 200 | 150 | 300 | 45000 | 12.5 to 40 | Semi Hermetic |  |  | R404A/R22 | 576 | 60549120 | 0 | 0 | 96 | 10091520 | 768 | 269107.2 | 480 | 50457600 | 1920 | 201830400
Distribution Centre | Cold Storage | 801 | up | - | - | - | - | - | - | Screw/Cetrifugal | 35403 | 222686 | Ammonia | 64 | 168752640 | 0 | 47065728 | 0 | 100158336 | 352 | 625150.976 | 224 | 106241280 | 640 | 607173120
[13 empty] | - | 9280 |  | 5104 |  | 8464 |  | 5184 |  | 3968 |  | 32000
31360
Assumptions: | [13 empty] | Estimated Energy Consumed Cool Rooms (excl. Cold Storage/Supermarket) GWh/a = | 315.9767
Rule of thumb; Medium Temp Coolroom = 250 & 300 W per m2
Ratio Med Temp to Low Temp, 80:20
COP = 2.5 (weighted av. of med/high temp)
Running time per day = 16 hrs
Av. life of Cond. Unit:
Small Commercial | 6
Commercial | 8
Condensing Units
Small Commercial | 25350 | 1.1941 | 30269.2257
Commercial | 4300 | 1.1941 | 5134.4249
MEPS 2000 | kWh/a | Weighted Av. kWh/a
Medium Temp | 15500 | 20860
Low Temp | 42300
Check use of Assumptions
Total Energy Consumed kWh/a= | 607173120
Total # Coolrooms = | 31360
Av. Energy Consumption kWh/a = | 19361.3878
Confirms reasonable to use rule of thumb of 250 & 300 W per m2, 80:20 Med:Low temp ratio, av. COP of 2.5 & typical running hrs of 16 per day
Note on A26: Mark Ellis & Ass, 2000 MEPS for Self Contained Commercial Refrig. Typical walk-in freezers are estimated to consume approximately 15,500 kWh per year, and typical walkin refrigerators approximately 42,300 kWh/yr.
Note on B22: Mark Ellis & Ass estimate Cool Room Condenser market to be 23,500 units in 2000
Note on P9: Assumed 70:30 split between Primary/Farm : Secondary Processing
This work-sheet calculates energy consumed by Coolrooms across the cold chain & excludes Cold Storage & Supermarket coolrooms as energy consumption in these areas are covered in work-sheets CC-Supermarket & CC-Cold Storage.
Energy Consumed Cool Rooms (excl. Cold Storage/Supermarket) was estimated to be 316 GWh/a
Base data on number of coolrooms was obtained from a survey undertaken by market leader of coolroom supplies (incl. insulating panels, etc.).
Assumptions are listed in the work sheet & a check was undertaken to confirm these assumptions versus technical data used by Mark Ellis & Ass in MEPS for Self Contained Commercial Refrigeration, 2000.

## CC-Industrial
Cold Food Chain: Industrial (Ammonia Systems)
Industrial refrigeration typically referred to “Ammonia refrigeration applications” in the Food Chain (Primary/Secondary Chilling/Freezing & Cold Storage), not to be confused with cooling/chiller applications in industry.
The installed base of industrial applications is difficult to quantify as the business is very project oriented, which means sales of Ammonia (screw & some large reciprocating) compressors & kWR sizes vary significantly from year to year. The best industry estimate is 120 to 150 compressors p.a. with approx. 30% applied in Cold Storage applications & the majority in chilling/Freezing/ice making applications in primary/secondary stages of the Cold Food Chain. The total energy consumed by Industrial refrigeration applications is likely to be at least double the energy consumed in Cold Storage (356 GWh/a) as there are more applications, typically require greater refrigeration capacity, however have lower annual running hours than Cold Storage applications due to seasonality/factory shifts. For simplicity until further investigation is undertaken we will assume the total energy consumed in primary/secondary stages of the Cold Food Chain is the same as Cold Storage (356 GWh/a & split 40:60 between primary : secondary).
The market leader of screw compressors in Australia is Mycom. Please see list/links of other suppliers below.
There are a group of key national contractors including Gordon Brothers (part of Hastie Group), Techrite Refrigeration, Cold Logic & regional contractors such as Fourair (target food chain applications Vic & Southern NSW) that service industrial refrigeration applications (Ammonia) & chillers (Food chain, Industrial Applications & Other).
Key suppliers
Compressors
http://www.mycomcpc.com/ (Mayekawa)
http://www.bitzer.de/home/index.php?LNG=EN&CTR=AUS&CMP=AUS&NAV=1&
York (http://www.frickcold.com/ , Stahl, Sabroe)
Howden, Grusso, Hitachi, Frascold, Hanbell
Contractors
http://www.gordonrefrig.com.au/ Part of Hastie Group http://www.hastiegroup.com.au/
http://www.ttrefrig.com.au/
http://www.coldlogic.com.au/
http://www.fourair.com/
http://www.heuch.com.au/
Components
http://www.apv.com/us/eng/APV+Home.htm
Industry Bodies
http://www.iiar.org/ International Institute of Ammonia Refrigeration

## CC-Merch
Product Type | Year | Energy Consumption (kWh/yr) | Quantity (Units) | Growth (%) | Value ($000) | Growth (%) | Av. Value | Est. Imported | Est. Av. Life (Yrs) | Existing Stock
Self Contained Commercial Refrig. Equip
Self-contained Display Cases | 2000 |  | 6000 | 3.3% |  |  |  |  | 6 | 36000
Glass Door Merchandisers | 2000 | 1899 | 10000 | [5 empty] | 8 | 170000
Reach in Refrigerators | 2000 | 1899 | 3500 | [5 empty] | 9 | 32000
Reach in Freezers | 2000 | 1786 | 4000 | [5 empty] | 9 | 36000
Ice Making Equipment | 2004 | 3922 | 4500 | 10% |  |  |  | 90% | 10 | 47500
Refrigerated Vending Machines | 2000 | 2740 | 13300 | [5 empty] | 9 | 120000
Ice Cream Displays | 2000 | 2388 | 10000 | [5 empty] | 6 | 60000
Cold Water Dispensers | 2000 |  | 32000 | [5 empty] | 9 | 300000
Ice Bins | 2004 | 0 | 1400 | 10% |  |  |  | 50% | 14 | 20000
821500
Note on A7: Data from MEPS Profile 2004
Note on A11: Data from MEPS Profile 2004
Note on C3: See data in Mark Ellis docs for supermarket self contained display cases.
Note on C7: Weighted average calculation based on proportion of small, medium & large
Note on C8: MEPS 2001 Doc, vending machines, seems high relative to merchandisers???
Note on C11: Not refrigerated, insulated pre-draining bins. Some have mechanical dispensing, etc that consume power.
The above data came from MEPS, Self Contained Commercial Refrigeration, 2000 & MEPS, Icemakers, 2004, Mark Ellis & Ass. This data would provide a good base for further analysis as was derived from various MEPS discussions. In the meantime have estimated Total Energy Consumed by self contained commercial refrigeration equipment to be 2,680 GWh/a in 2006. Based on estimate in Ellis report of 2,200 GWh/a & applying a 4.8% growth rate.

## CC-Ref Transport
Refrigeration Transport Product Type | Av. Size Cooling (kW) | Quantity (Units) p.a. | Growth (%) | Est. Av. Life (Yrs) | Existing Stock | Running Hrs p.a. | CO2-e
Trailer & Inter-Modal: Refrigeration | 18 | 700 | 7% | 6 to 7.5 | 3451.5907 | 4000
Diesel Drive: Truck Refrigeration | 4 to 10 | 500 |  | 6 to 9 | 2754.6439 | 4000
Off Engine/Vehicle Powered Refrigeration (Option Electrical Stand-by) | 1 to 5 | 1800 |  | 6 to 10 | 10211.8416 | 4000
Refrigerated Containers (20ft & 40ft Marine Containers) | - | - | - | - | - | -
Total Refrigerated Transport |  | 3000 |  |  | 16418.0763
| 2006 | % Vehicles with Refrig.
Light commercial vehicles | 2114333 | 0.483%
Rigid trucks | 383546 | 0.7182%
Light | 95452 | -
Heavy | 288094 | -
Articulated trucks | 71680 | 4.815%
[10 empty] | 2006 | Av. Growth p.a. % | Av. Growth p.a. (units)
| 1995 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005
Light commercial vehicles | 1527212 | 1531748 | 1721200 | 1696631 | 1719654 | 1810071 | 1879755 | 1940180 | 2030254 | 2114333 | 3.8% | 80344.654
Rigid trucks | 337421 | 339021 | 346823 | 346628 | 332102 | 341651 | 348673 | 358704 | 368520 | 383546 | 2.9% | 11122.834
Light | [8 empty] | 88768 | 95452 | - | -
Heavy | [8 empty] | 279752 | 288094 | - | -
Articulated trucks | 58322 | 58858 | 63295 | 61117 | 61502 | 61519 | 64261 | 66197 | 69723 | 71680 | 2.9% | 2078.72
Non freight trucks | 46971 | 17614 | 17697 | 18714 | 18980 | 17504 | 18599 | 17616 | 19962 | 20293 | - | -
Total trucks | 442714 | 415493 | 427815 | 426459 | 412584 | 420674 | 431533 | 442517 | 458205 | 475519 | -
Buses | 52170 | 53298 | 65891 | 55805 | 55078 | 56754 | 70122 | 61728 | 72620 | 73375 | 1.8% | 1320.75
Existing Stock Calculations
| Existing Stock | Growth (%) | 2006 | 2005 | 2004 | 2003 | 2002 | 2001 | 2000 | 1999 | 1998 | 1997
| - | 7% | 700 | 651 | 605.43 | 563.0499 | 523.6364 | 486.9819 | 452.8931 | 421.1906 | 391.7073 | 364.2878
| % in Service | - | 1 | 1 | 1 | 0.9 | 0.8 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2
| 3451.5907 |  | 700 | 651 | 605.43 | 506.7449 | 418.9091 | 243.4909 | 90.5786 | 84.2381 | 78.3415 | 72.8576
| Existing Stock | Growth (%) | 2006 | 2005 | 2004 | 2003 | 2002 | 2001 | 2000 | 1999 | 1998 | 1997
| - | 7% | 500 | 465 | 432.45 | 402.1785 | 374.026 | 347.8442 | 323.4951 | 300.8504 | 279.7909 | 260.2055
| % in Service | - | 1 | 1 | 1 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.2 | 0.2
| 2754.6439 |  | 500 | 465 | 432.45 | 361.9606 | 299.2208 | 243.4909 | 194.0971 | 150.4252 | 55.9582 | 52.0411
| Existing Stock | Growth (%) | 2006 | 2005 | 2004 | 2003 | 2002 | 2001 | 2000 | 1999 | 1998 | 1997
| - | 7% | 1800 | 1674 | 1556.82 | 1447.8426 | 1346.4936 | 1252.2391 | 1164.5823 | 1083.0616 | 1007.2473 | 936.7399
| % in Service | - | 1 | 1 | 1 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3
| 10211.8416 |  | 1800 | 1674 | 1556.82 | 1303.0583 | 1077.1949 | 876.5673 | 698.7494 | 541.5308 | 402.8989 | 281.022
Note on A2: Application: Articulated Trailers up to 48ft long
Note on A3: Application: Rigid Market 3 to 8 ton Trucks (6/8/10/12/1416/18 Pallet, Insulated or Curtain
Note on A4: Application: 1 to 4 ton Trucks
Note on A5: Refrigerated Marine Containers are generally not considered part of the rolling stock of refrigerated transport as it enters/exists via port. They do travel inland to dispatch goods & transport coys are purchasing generator sets to accommodate journey. Aust Bureau of Statistics in quoted that 3% of containers are refrigerated based on tonnage moved p.a. refer article 9220.0 Freight Movements, Australia, Summary
Note on A9: Australian Bureau of Statistics, Survey of Motor Vehicle Use, Cat No 9208.0, various (Not incl. campervans).
Note on A19: Australian Bureau of Statistics, Survey of Motor Vehicle Use, Cat No 9208.0, various (Not incl. campervans).
Note on B1: kW rating @ 2 Deg Celsius
Note on C6: Carrier Transicold believe closer to 2000p.a, however Thermoking's estimate is probably closer as there are lots of smaller players offering equipment in this product segment
Note on C15: ABS estimate 3% of bulk shipping containers to be refrigerated, expect Articulated trucks to be slightly higher.
Note on F1: Existing stock of Refrigerated Transport was estimated by Price Waterhouse to be 5,000 units in 1994. Equiv. to 11,250 with a growth rate of 7% p.a. over 12 years.
Note on L18: ABS9309.0 Av. Growth rate from 2002 to 2006

## Auto Air
Direct Energy Consumed from Auto Air Cond | [13 empty] | Transport vehicle air pollution, 2000
| No of vehicles 2005 | annual distance 2005 | Fuel Consumed in 2005 (Million Litres) |  | Av. Annual Growth Rate | Mill Litres Due to A/C 2006 | t CO2-e pa fuel combustion | New vehicle HFC-134a charge (kg) | Av HFC-134a charge in use (kg) | tCO2-e pa refrigerant leakage | Assumptions: |  |  |  | Carbon monoxide (kt) | % | NxO (kt) | % | Volatile organic compunds (kt) | %
| million | mill km | Total | Due to A/C | [9 empty] | Cars | 2777 | 78 | 261 | 45 | 416 | 78.9
Passenger vehicles | 11.011 |  | 18144 |  |  |  |  | 0.7 | 0.5 | 1316915.6 | AC Penetration (all types, excl Mcycl) | 92% |  | Light commercial vehicles | 543 | 15.2 | 66 | 11.4 | 67 | 12.7
petrol |  | n/a | 15856 | 437.6256 | 2.6% | 449.0039 | 1077609.2774 |  |  |  | Majority passenger vehicle use is within urban areas
diesel |  | n/a | 1081 | 29.8356 | 2.6% | 30.6113 | 82650.5791 |  |  |  | Av fuel con increase for cars with A/C | 3%
LPG/CNG |  | n/a | 1207 | 33.3132 | 2.6% | 34.1793 | 54686.9491 |  |  |  | Av fuel con increase for rigid trucks with A/C | 1.6889 | L/100km | 0.8
Light commercial vehicles | 1.996 | n/a | 4484 |  |  |  |  | 0.7 | 0.5 | 238721.6 | Av fuel con increase for artic trucks with A/C | 0.84444 | L/100km | Trucks - rigid and other | 61 | 1.7 | 56 | 9.7 | 17 | 3.2
petrol |  | n/a | 2699 | 74.4924 | 3.8% | 77.3231 | 185575.4669 |  |  |  | Av. Fuel Consumed Running A/C | 10%
diesel |  | n/a | 1472 | 40.6272 | 3.8% | 42.171 | 113861.7907 |  |  |  | Av. Operating Time of A/C | 15%
LPG/CNG |  | n/a | 313 | 8.6388 | 3.8% | 8.9671 | 14347.319 |  |  |  | Mobile aircon refrigerant loss | 20% | pa
Rigid trucks - diesel | 0.367 | 7671 | 2234 | 129.5547 | 2.9% | 133.3118 | 213298.8032 | 1.2 | 0.84 | 73740.576 | Assumes all HFC-134a |  |  | Trucks - articulated | 36 | 1 | 79 | 13.6 | 10 | 1.9
Articulated trucks - diesel | 0.069 | 6308 | 3452 | 53.2676 | 2.9% | 54.8123 | 87699.7035 | 1.2 | 0.84 | 13864.032 |  |  |  | Buses | 18 | 0.5 | 17 | 2.9 | 5 | 0.9
Non freight trucks - diesel | 0.02 | 286 | 65 | 4.8302 | 1.9% | 4.922 | 7875.1943 | 1.2 | 0.84 | 4018.56 |  |  |  | Motorcycles | 24 | 0.7 | 1 | 0.2 | 5 | 9
Buses - diesel | 0.062 | 1856 | 506 | 13.9656 | 1.8% | 14.217 | 22747.1693 | 10 | 7 | 103812.8 |  |  |  | Total | 3459 | 97.1 | 479 | 82.8 | 520 | 98.5
Motorcycles - petrol |  | n/a | 83 | 0 | 5.7% | 0 | n/a | n/a
TOTAL |  |  | 28885 | 826.1508 |  | 849.5188 | 1860352.2526 |  |  | 1751073.168
Total av % Fuel Consumed Due to A/C = |  | 2.86%
Registered vehicles by type
| 1984 | 1995 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004
Passenger vehicles | 6636200 | 8628806 | 9336395 | 9686223 | 9711320 | 9861807 | 10194637 | 10365941 | 10654328
Light commercial vehicles | 1121000 | 1527212 | 1531748 | 1721200 | 1696631 | 1719654 | 1810071 | 1879755 | 1940180
Rigid trucks | 520600 | 337421 | 339021 | 346823 | 346628 | 332102 | 341651 | 348673 | 358704
Articulated trucks | 49100 | 58322 | 58858 | 63295 | 61117 | 61502 | 61519 | 64261 | 66197
Non freight trucks | 47200 | 46971 | 17614 | 17697 | 18714 | 18980 | 17504 | 18599 | 17616
Total trucks | 616900 | 442714 | 415493 | 427815 | 426459 | 412584 | 420674 | 431533 | 442517
Buses | 60500 | 52170 | 53298 | 65891 | 55805 | 55078 | 56754 | 70122 | 61728
Motorcycles | 398400 | 296628 | 307954 | 33782 | 337793 | 349465 | 367258 | 377271 | 392648
TOTAL | 8832800 | 10947530 | 11644888 | 11934911 | 12228008 | 12398588 | 12849393 | 13124622 | 13491401
Total number of registered vehicles ('000)
Year | NSW | Vic. | Qld | SA | WA | Tas. | NT | ACT | Australia
2004 | 4063.64 | 3565.15 | 2656.044 | 1095.923 | 1480.206 | 350.403 | 106.016 | 215.689 | 13533.071
2003 | 3944.85 | 3494.314 | 2552.061 | 1077.154 | 1438.441 | 338.484 | 104.259 | 213.396 | 13162.959
2002 | 3847.132 | 3413.708 | 2445.524 | 1063.058 | 1405.676 | 335.057 | 103.795 | 208.011 | 12821.961
2001 | 3745.537 | 3317.682 | 2354.352 | 1050.567 | 1371.341 | 331.073 | 102.824 | 203.391 | 12476.767
2000 | - | - | - | - | - | - | - | - | -
1999 | 3679.333 | 3266.492 | 2315.634 | 1032.536 | 1344.809 | 329.568 | 103.174 | 197.033 | 12268.579
1998 | 3682.636 | 3177.39 | 2228.844 | 1031.06 | 1327.203 | 322.695 | 102.195 | 194.834 | 12066.857
1997 | 3530.148 | 3118.967 | 2132.157 | 992.211 | 1269.581 | 324.983 | 99.107 | 197.238 | 11664.393
1996 | 3448.9 | 3050.2 | 2082 | 984.5 | 1225 | 325.5 | 96.191 | 188.8 | 11401.1
1995 | 3332.461 | 2869.88 | 2012.88 | 962.824 | 1175.487 | 319.873 | 90.37 | 183.755 | 10947.53
1994 | 3262.5 | 2808.1 | 1975.1 | 920.2 | 1142.4 | 316.1 | 91.9 | 182.8 | 10699.2
1993 | 3235 | 2718.4 | 1894.9 | 904.6 | 1111 | 310.7 | 83.7 | 173.1 | 10431.5
1992 | 3207.8 | 2684.8 | 1832.8 | 889.5 | 1081.8 | 304.1 | 80.8 | 165.2 | 10246.9
1991 | 3058.8 | 2775.2 | 1643.3 | 857.8 | 1062.9 | 298.2 | 75.2 | 156.7 | 9934.1
1990 | 3223.8 | 2652.2 | 1751.9 | 883.5 | 1037.6 | 294.1 | 79.5 | 158.1 | 10080.6
1989 | 3171.4 | 2585.2 | 1693.4 | 862.6 | 986.3 | 284.5 | 76.7 | 146.2 | 9806.1
1988 | 3081.2 | 2575.2 | 1616.2 | 846.3 | 935.7 | 278.1 | 72.5 | 139.1 | 9544.4
1987 | 3041.8 | 2529.4 | 1575.3 | 834.9 | 906.1 | 274.9 | 77 | 134.4 | 9373.7
1986 | 3043.1 | 2476.8 | 1567.4 | 835.9 | 887.3 | 273.2 | 75.3 | 131.6 | 9290.5
1985 | 2984.9 | 2437.7 | 1546.1 | 816.9 | 866.3 | 266.5 | 71.8 | 128.1 | 9118.3
1984 | 2890.8 | 2341.8 | 1533.5 | 790.2 | 830 | 255.9 | 67 | 123.6 | 8832.8
1983 | 2835.6 | 2257.7 | 1496.1 | 763.7 | 809.3 | 249.3 | 61.9 | 116.2 | 8589.8
1982 | 2784.1 | 2171.8 | 1439.5 | 744.7 | 789.1 | 246.6 | 58.2 | 112 | 8346
1981 | 2626.9 | 2035.9 | 1355.9 | 725.4 | 773.2 | 237.3 | 53.6 | 109.6 | 7917.6
1980 | 2520.9 | 1960.2 | 1256.9 | 708.6 | 745 | 229.5 | 47 | 105.5 | 7573.6
1979 | 2413.2 | 1974 | 1183.4 | 689.3 | 719.7 | 226.6 | 45.6 | 106.6 | 7358.3
1978 | 2330.6 | 1915.4 | 1129.6 | 681.3 | 695.5 | 218.1 | 46.9 | 97 | 7114.5
1977 | 2252.5 | 1829.2 | 1067.2 | 668 | 654.9 | 209.4 | 38.1 | 98.7 | 6818
1976 | 2194.1 | 1799.6 | 1012.2 | 641 | 604.8 | 202.8 | 34.1 | 92.2 | 6580.9
1975 | 2148.8 | 1715.9 | 918 | 617.3 | 564.4 | 194.3 | 31.8 | 85.9 | 6276.4
1974 | 2043 | 1620.4 | 889.7 | 577.6 | 523 | 182.6 | 36.7 | 79.7 | 5952.7
1973 | 1944.3 | 1523.8 | 827 | 547.1 | 488.6 | 174.5 | 34.2 | 73.6 | 5613.1
1972 | 1848.4 | 1445.4 | 774 | 516.5 | 465.1 | 167.8 | 32 | 67.9 | 5317.1
1971 | 1739.8 | 1379.3 | 726.5 | 496.8 | 445.6 | 161.3 | 28.7 | 61.2 | 5039.2
1970 | 1648.3 | 1314.7 | 686.1 | 478.3 | 411.7 | 154.3 | 25 | 53.2 | 4771.6
1969 | 1555.7 | 1248.6 | 649.9 | 456.5 | 379.4 | 148.7 | 22.5 | 47.1 | 4508.4
1968 | 1482.1 | 1188.5 | 620.9 | 432.1 | 352 | 141 | 19.9 | 42.8 | 4279.3
1967 | 1437.3 | 1136.5 | 590 | 413.1 | 337.1 | 135.1 | 17 | 40.4 | 4106.6
1966 | 1369 | 1092.9 | 564.5 | 399.1 | 313 | 129.2 | 15.5 | 36 | 3919.5
1965 | 1312.6 | 1049.8 | 536.9 | 384.7 | 291.5 | 122.5 | 14.1 | 32.1 | 3744.3
1964 | 1230.7 | 989.9 | 497.9 | 363.7 | 277.9 | 114.6 | 13.3 | 28.1 | 3516.2
1963 | 1157.4 | 931.5 | 459 | 342.9 | 258.2 | 107.4 | 11.2 | 24.2 | 3291.9
1962 | 1088.4 | 876.6 | 431.7 | 328.6 | 242.1 | 102.6 | 10.1 | 20.5 | 3100.7
1961 | 1031.1 | 844.7 | 418.6 | 318.5 | 225.2 | 97.4 | 9.3 | 17.9 | 2962.7
1960 | 977.8 | 802.9 | 404 | 309.8 | 212.1 | 93.2 | 8.3 | 15.9 | 2824.2
1959 | 919.4 | 749.9 | 381.9 | 290.8 | 198.4 | 87.7 | 7.4 | 13.7 | 2649.1
1958 | 865.3 | 711.7 | 363.9 | 274.8 | 188.1 | 83.8 | 6.8 | 11.9 | 2506.2
1957 | 807.9 | 675.5 | 344.4 | 262.5 | 180.6 | 78.6 | 5.9 | 10.6 | 2366.1
1956 | 759.8 | 647.2 | 326.3 | 248.2 | 174.9 | 74.7 | 5.2 | 9.9 | 2246.3
1955 | 709 | 629.1 | 307.7 | 229.5 | 168.8 | 71.7 | 4.9 | 8.8 | 2129.7
1954 | 654.5 | 559.2 | 284.2 | 218.4 | 153.9 | 65.3 | 3.8 | 7.8 | 1947.3
1953 | 613.5 | 539.8 | 266.2 | 205.7 | 141.9 | 60.5 | 5.1 | 6.9 | 1839.9
1952 | 590.5 | 533.2 | 255 | 192.3 | 132.9 | 55.1 | 4.7 | 6.2 | 1770.2
1951 | 544.3 | 444.4 | 240.7 | 173 | 118.6 | 49.1 | 4.3 | 5.5 | 1580.4
1950 | 478 | 399.8 | 212.9 | 151.9 | 103.3 | 42.7 | 3.7 | 4.3 | 1397.1
Note on A7: user: assume mainly LPG
Note on A33: Source: From 1995 vehicle registration data was sourced from the ABS Motor Vehicle Census (9309.0) as the Motor Vehicle Registrations publication was discontinued. Data exclude plant equipment, caravans and trailers.
Note on C17: 64.6% of fuel was petrol and 30.0% was diesel fuel.
Note on D4: Passenger vehicles used 15,856 million litres of petrol in the 12 months ended 31 October 2005, of which 95.6% (15,160 million litres) was unleaded petrol. Remainder was Diesel.
Note on D12: Assume 100% diesel. 2185 million litres of diesel fuel was used by rigid trucks.
Note on D14: user: Assume all diesel. Actual: 60 million litres of diesel.
Note on D15: user: Assume mainly diesel. Actual 435 mill L diesel
Note on E15: user: assume bus A/C fuel use is similar proportion of total fuel use as per car.
Note on F2: ABS9309.0 Av. Growth rate from 2002 to 2006
Note on I15: user: based on small coach = 4.2 kg & large = 22kg source?
Note on K5: user: need amount of refrigerant per vehicle * number of vehicles * 20% * GWP
Note on L6: user: assume same for LCVs
Note on L10: Best Guess, requires study to qualify more accurate estimate by vehicle type
Note on L12: user: data needed on hydrocarbon refrigerant market share
Note on N7: user: Assume rigid truck cab has similar A/C load as car. Car fuel can increase due to A/C while in use: 0.8 gallons/100 miles see US EPA ref in text box
Note on N8: user: assume artic has half A/C load of rigid truck because of predominantly highway use plus nighttime driving
Comments:
There is a history of a lack of available information in the Auto Air industry, including an attempt to undertake a study by Price Waterhouse. Unfortuantely, the researcher was unable to gain the confidence of the industry & failed to collect information of any significance.
Plan recommended by VASA
Step 1: Collect base information
Step 2: Target areas of interest with Focus Groups (ie half a dozen people who live & breath auto air), plus surveys to members
Step 3: Overview review by keystakeholders in Auto Air industry
VASA would fully support this process
% Vehicles in the garage with AC, source ABS4602.0 Environmental Views: People's Views & Practices, 2006
pp 8, In March 2006, 90% of households in Australia kept at least one registered motor vehicle in their garage or dwelling and 51% had two or more. The majority (92%) of these registered motor vehicles in the garage have airconditioning.
No. of Passenger Vehicles in Australia in 2006:- 11,188,880
ABS: http://www.abs.gov.au/AUSSTATS/abs@.nsf/productsbyCatalogue/06D0E28CD6E66B8ACA2568A900139408?OpenDocument
pp 49, Airconditioning has become a standard feature in motor vehicles across Australia. In April 1996, 72% of motor vehicles in Australia had airconditioning. In March 2006, however, the proportion has increased significantly to 92%. Motor vehicles without airconditioning were most likely to be found in Tasmania (only 79% of households), but this level has more than doubled since 1996 (37%) (graph 3.6 and table 3.13, pp 57, Number of Registerd Motor Vehicles with Air Conditioning, 1996:2006).
pp 53, Total no of registered motor vehicles kept in 7,944,700 kept in dwellings or garage, see Tables 3.8 & 3.9.
Motor Vehicle Use, Fuel Consumption, source ABS9208.0 Survey of Motor Vehicle Use, 2004
Passenger vehicles used 14,882 million litres of petrol in the 12 months ended 31 October 2004, of which 94.2% (14,021 million litres) was unleaded petrol. A total of 5,384 million litres of diesel fuel was used by articulated and rigid trucks. This was 65.3% of all diesel fuel used and represents 100.0% and 97.9% respectively of fuel consumption for these vehicle types. The total fuel consumption by other vehicles in the 12 months ended 31 October 2004 included 4,471 million litres of fuel by light commercial vehicles and 524 million litres of fuel by buses.
Motor Vehicle Stats, source ABS9309.0 Motor Vehicle Census, 2006, (PB Can be used to update tables to 2006).
Air Conditioning Fuel Consumption, source www.mynrma.com.au, NRMA’s Top Tips for reducing emissions and petrol use, Tip 3. In urban areas when the weather is fine, switch-off the airconditioning and open the windows - this reduces fuel consumption by up to 10%. At higher speeds, open windows can create as much drag as airconditioning so there’s little advantage in turning airconditioning off.
Source: http://www.iea.org/textbase/work/workshopdetail.asp?WS_ID=247, www.epa.gov/fueleconomy/420d06002.pdf
Average increase in fuel consumption of 26% for conventional (non-hybrid) vehicle while airconditioning on. This translates to 3-4% increase in annual city fuel consumption and 1-2% increase in highway consumption.
Air Conditioning Refrigerant Leakage http://refrigerants.dupont.com/Suva/en_US/pdf/k10795.pdf
Main refrigerant is HFC-134a. 20% of in vehicle refrigerant stock is released to atmosphere each year: 60% from service and end-of-life; 40% from system leaks.
IEA study cites modern car aircon refrigerant charges (presumably from new) of 550-900g HFC-134a which is overcharged from the optimum of 250-300g. This overcharge is more than sufficient to cover the entire lifetime of the vehicle in normal conditions. Australian industry sources indicate about 700g initial charge. We propose a reasonable figure for average in use charge of about 500g for stock estimation purposes.
www.iea.org/textbase/work/2006/car_cooling/Session3/3b%20Clodic%20New%20evidence%20on%20leakage.pdf
in www.iea.org/Textbase/work/workshopdetail.asp?WS_ID=247
Av. Age of Vehicles on road, source ABS9309.0 Motor Vehicle Sensis, 2006
Campervans were the oldest vehicles registered with an average age of 18.9 years, while motorcycles were the youngest vehicle type with an average age of 9.4 years. The average age of passenger vehicles dropped slightly from 10.1 years in 2002 to 9.8 years in 2006, with 21.0% of passenger vehicles manufactured before 1991. Includes buses, all categories of trucks, etc.

## Domestic Appliances
Domestic Appliances
Ownership (Ratio of Existing Stockto the # Households)
Number of Households (000's) | Qld | NSW & ACT | Vic | Tas | NT | SA | WA | Aust
Family households: 2003 | 1465.7 | 2648.9 | 1880.4 | 194.2 | 55.3 | 627.2 | 768.5 | 7640.2
Projected Family Households, 2006 | 1583.1 | 2773.3 | 1975.6 | 202.8 | 67.2 | 649 | 806.3 | 8057.3
Stock of Refrigerators and Freezers* | 2554242.7364 | 4474563.4394 | 3187519.3924 | 327206.3843 | 108423.4173 | 1047124.9674 | 1300919.6629 | 13000000
National average per Household | [7 empty] | 1.6134
Replacement rate (10yr av life) | 10% |  |  |  | Sales for replacements |  |  | 1300000
Total Dwellings approved 04-05^ | 159102 |  |  |  | Sales for new Dwelling (at national average) |  |  | 256702.1211
Estimate total sales 2006 | [7 empty] | 1556702.1211
[5 empty] | Average Value |  |  | 480
[5 empty] | Total Purchases 2006 |  |  | 747217018.1078
Note on A2: Ownership can exceed 1.0
Note on A3: Sources: ABS4442.0 Family Characteristics - June 2003 ABS3236.0 Household & Family Projections - 2001 to 2026
*"The estimated 13 million of refrigerators and freezers household refrigerators (in Australia) use about 24% of the electricity consumed by all domestic electrical appliances, equaling lighting (Energy Efficient Strategies, 2006; James, 2003). Refrigerators and freezers were estimated to account for nearly 17% of all greenhouse gas emissions in 2000. Although Australia has developed minimum energy performance standards for domestic refrigeration, there is still considerable technical potential to improve the energy efficiency of refrigerated appliances."
Original work quoted in 'ELECTRICITY USAGE IN THE AUSTRALIAN COLD CHAIN'
Silvia Estrada-Flores1, PhD and Glenn Platt2, PhD
Food Science Australia (a joint venture of CSIRO and the Victorian Government).
PO Box 52, North Ryde NSW 1670, Australia
NB - No time was invested in the course of the 'Chilling Insights' project to further validate this original estimate.
"In Australia, household refrigeration accounted for about 8,330 GWh of electricity use and 9.06 million tonnes of carbon dioxide-equivalent (Mt CO2-e) emissions in 2000 (Energy Consult, 2006). About 20% of this was due to freezers, and 80% to refrigerators (fresh food only) and refrigerator-freezers. Considering that refrigerator and freezer sales have increased by 2.6% per year (Energy Efficient Strategies, 2006), estimates for 2005 would be closer to 9,470 GWh per year."
Orignal work quoted by CSIRO Division of Energy Technology. PO Box 330. Newcastle, NSW 2300 Australia
^http://www.abs.gov.au/ausstats/abs@.nsf/Previousproducts/1F455D0207F68721CA2570DE00185F72?opendocument

## Comp-Cond Unit-Data
Compressors (AC & Refrig) & Refrig. Condensing Unit Data
Product Type | Av. Size Cooling (kW) | Quantity (Units) p.a. | Growth (%) | Est. Av. Life (Yrs)
Compressors:
Domestic/small com |  | 58500 |  | 7
Commercial: Refrig |  | 29750 | 4.8% | 10
Supermarket |  | 1200 |  | 17
Commercial: A/C |  | 63000 |  | 10
Large Reciprocating Compressors |  | 600 |  | 25
Screw (Ammonia) | 30 - 200kW | 120 |  | 25
Condensing Units
Small Commercial |  | 25350 | 4.8% | 8
Commercial |  | 4300 |  | 10
Rack Systems |  | 100 |  | 25
Note on A3: 2002 Data 80% Medium Temp 20% Low Temp - Freezer
Note on A7: Commercial AC compressors are used in RT Units, Ducted & other equipment. Market leader sells 75,000 into Aust & NZ & has up to 95% market share.
Note on A9: Key suppliers include: Mycom (Mayekawa), Bitzer, York (incl. Frickcold, Stahl, Sabroe), Howden, Grusso, Hitachi, Frascold, Hanbell
Note on A10: 2002 Data from Market Leader/supplier of Condensing Units. 80% Medium Temp 20% Low Temp - Freezer
Note on A14: 9 or 10 Compressors per Supermarket
Note on C6: 90-120 stores p.a.over last 5 years 10 Compressors/store 15% Repairs/Referb
The above data was provided by market leaders/suppliers & has been used to check data or assumptions in other work-sheets.
For example annual AC equipment sales data cross checked with 63,000 A/C compressors sold p.a. in Aust in 2006 by market leader.
Split System Applications = 148,217 p.a. x 0.3 locally manf. x 1 per unit x 0.95 market share= 42,242
RT Packages Applications = 5,194 p.a. x 0.6 locally manf. x 3 per unit x 0.7 market share = 6,544
Spares = 0.12 x 63,000 = 7,560
Swimming Pool HP = 900 x 0.95 = 855
Other Manufactured Applications = 5,799 = less than 10%
Confirms annual data for Split Systems & RT Packages is correct order of magnitude & study has not overlooked more than 10% of miscellaneous applications using A/C compressors

## Refrigerant-Check
Volumes and approximate values of bulk refrigerant gas imports is available. Requests have been made to get industry estimates of the proportion of various end uses. Without that information the import volumes do not add much understanding to the rest of the data.

## AC Calculation WSheet
AC Calculation Sheet (Regional Splits/Existing Stock/Average Size)
Regional Split Calculations | [8 empty] | Existing Base Calculation | [43 empty] | Average Size Calculations
Split Ducted Outdoor Units | [8 empty] | Product Type | Quantity (Units) p.a. | Growth (%) | Growth (%) | Growth (%) | Est. Av. Life (Yrs) | Accelerate Retirement % | Existing Stock | 2006 | 2005 | 2004 | 2003 | 2002 | 2001 | 2000 | 1999 | 1998 | 1997 10 Years | 1996 | 1995 | 1994 | 1993 | 1992 15 Years | 1991 | 1990 | 1989 | 1988 | 1987 20 Years | 1986 | 1985 | 1984 | 1983 | 1982 25 Years | 1981 | 1980 | 1979 | 1978 | 1977 30 Years | 1976 | 1976 | 1976 | 1976 | 1976 35 Years |  | Split Systems
Year | QLD | NSW | VIC | TAS | SA | NT | WA | Total | Split Systems | 148216.6667 | 15% |  |  | 12 | 0% | Sold | 148216.6667 | 129351.1111 | 139368.8889 | 88026.6667 | 86666.6667 | 78333.3333 | 70000 | 61666.6667 | 53333.3333 | 45000 | 45000 | 45000 | [24 empty] | Heat Pump | Up to 2.5 | 53 | Cooling Only | Up to 2.5 | 1 | 54 | 2.5 | 135
Split Ducted Outdoor Units NSW: & ACT; Split Ducted Outdoor Units SA: & BH | [7 empty] | Growth | 148217 | 125984.1667 | 109948.4444 | 118463.5556 | [33 empty] | >2.5 to 4 | 1252 |  | >2.5 to 4 | 40 | 1292 | 4 | 5168
2005 | 27041 | 41211 | 15333 | 2504 | 12967 | 2027 | 15333 | 116416 | [7 empty] | Imported | 103752 | 88476 | 92959 | 57217 | 52000 | 47000 | 42000 | 37000 | 32000 | 27000 | 27000 | 27000 | [25 empty] | >4 to 7.5 | 17155 |  | >4 to 7.5 | 614 | 17769 | 7.5 | 133267.5
| 23.23% | 35.4% | 13.17% | 2.151% | 11.14% | 1.741% | 13.17% | 100% | [7 empty] | % Imported | 70% | 68.4% | 66.7% | 65% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | [25 empty] | >7.5 to 10 | 21178 |  | >7.5 to 10 | 904 | 22082 | 10 | 220820
2006 | 29405 | 47958 | 18204 | 2585 | 15971 | 1236 | 18036 | 133395 | [7 empty] | % in Service | 100% | 100% | 100% | 100% | 95% | 90% | 85% | 80% | 75% | 70% | 65% | 60% | [25 empty] | >10 to 12.5 | 17672 |  | >10 to 12.5 | 883 | 18555 | 12.5 | 231937.5
| 22.04% | 35.95% | 13.65% | 1.938% | 11.97% | 0.9266% | 13.52% | 100% | [7 empty] | 838130 | 148216.6667 | 129351.1111 | 139368.8889 | 88026.6667 | 82333.3333 | 70500 | 59500 | 49333.3333 | 40000 | 31500 | 29250 | 27000 | [25 empty] | >12.5 to 15.5 | 24532 |  | >12.5 to 15.5 | 2027 | 26559 | 15.5 | 411664.5
Av. | 22.64% | 35.68% | 13.41% | 2.044% | 11.56% | 1.334% | 13.35% | 100% | VRV Systems | 3000 | 25% |  |  | 15 |  | Sold | 3000 | 2250 | 1687.5 | 1181.25 | 826.875 | 578.8125 | 405.1687 | [30 empty] | >15.5 to 18 | 25099 |  | >15.5 to 18 | 904 | 26003 | 18 | 468054
Split Ducted Outdoor Units Year: RT Package | [7 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 100% | 100% | [30 empty] | Total Up to 18 | 106941 |  | Total Up to 18 | 5373 | 112314
Year | QLD | NSW | VIC | TAS | SA | NT | WA | Total | [7 empty] | 9929.6063 | 3000 | 2250 | 1687.5 | 1181.25 | 826.875 | 578.8125 | 405.1687 | [30 empty] | >18 to 25 | 8307 |  | >18 to 25 | 75 | 8382 | 25 | 209550
RT Package NSW: & ACT; RT Package SA: & BH | Wall Hung Split Systems | 874000 | 20.25% | 30% | 15% | 10 |  | Method 1 | 874000 | 697015 | 555869.4625 | 443305.8963 | 310314.1274 | 217219.8892 | 152053.9224 | 106437.7457 | 90472.0839 | 76901.2713 | [27 empty] | >25 to 30 | 2608 |  | >25 to 30 | 72 | 2680 | 30 | 80400
2005 | 1015 | 891 | 1331 | 26 | 315 | 95 | 456 | 4129 | [7 empty] | Method 2 | 874000 | 697015 | 555869.4625 | 443305.8963 | 286000 | 141000 | 126000 | 111000 | 96000 | 81000 | [5 empty] | 80000 | [21 empty] | >30 to 37.5 | 631 |  | >30 to 37.5 | 45 | 676 | 37.5 | 25350
| 24.58% | 21.58% | 32.24% | 0.6297% | 7.629% | 2.301% | 11.04% | 100% | [7 empty] | Av. | 874000 | 697015 | 555869.4625 | 443305.8963 | 298157.0637 | 179109.9446 | 139026.9612 | 108718.8729 | 93236.0419 | 78950.6356 | [27 empty] | >37.5 to 45 | 486 |  | >37.5 to 45 | 37 | 523 | 45 | 23535
2006 | 1029 | 1018 | 1494 | 22 | 359 | 98 | 655 | 4675 | [7 empty] | % in Service | 100% | 100% | 100% | 100% | 94% | 88% | 82% | 76% | 68% | 60% | [27 empty] | >45 to 65 | 434 |  | >45 to 65 | 48 | 482 | 65 | 31330
| 22.01% | 21.78% | 31.96% | 0.4706% | 7.679% | 2.096% | 14.01% | 100% | [7 empty] | 3315474.0915 | 874000 | 697015 | 555869.4625 | 443305.8963 | 280267.6399 | 157616.7513 | 114002.1082 | 82626.3434 | 63400.5085 | 47370.3814 | [27 empty] | >65 to 77.5 | 170 |  | >65 to 77.5 | 12 | 182 | 77.5 | 14105
Av. | 23.3% | 21.68% | 32.1% | 0.5501% | 7.654% | 2.199% | 12.53% | 100% | Window/Wall Units | - |  |  |  | 12 |  | Imported | 166807 | 147987 | 316910.5375 | 322254.1037 | 211288 | 176527 | 101882 | 151714 | 195556 | 123800 | 120000 | 120000 | [25 empty] | >77.5 to 90 | 61 |  | >77.5 to 90 | 9 | 70 | 90 | 6300
RT Package Year: Wall Mounted Split Systems | [7 empty] | % Imported | 100% | 100% | 100% | 100% | 80% | 80% | 70% | 70% | 70% | 60% | 55% | 50% | [25 empty] | >90 to 120 | 58 |  | >90 to 120 | 27 | 85 | 120 | 10200
Year | QLD | NSW | VIC | TAS | SA | NT | WA | Total | [7 empty] | Total | 166807 | 147987 | 316910.5375 | 322254.1037 | 264110 | 220658.75 | 145545.7143 | 216734.2857 | 279365.7143 | 206333.3333 | 218181.8182 | 240000 |  |  |  | 230000 | [21 empty] | >120 to 160 | 11 |  | >120 to 160 | 6 | 17 | 160 | 2720
Wall Mounted Split Systems NSW: & ACT; Wall Mounted Split Systems SA: & BH | [7 empty] | % in Service | 100% | 100% | 100% | 95% | 90% | 85% | 80% | 75% | 70% | 65% | 60% | 55% | [25 empty] | Over 160 | 6 |  | Over 160 | 15 | 21 | 250 | 5250
2006 | 208954 | 176753 | 133751 | 10915 | 41798 | 13847 | 69482 | 655550 | [7 empty] | 2234673.9168 | 166807 | 147987 | 316910.5375 | 306141.3985 | 237699 | 187559.9375 | 116436.5714 | 162550.7143 | 195556 | 134116.6667 | 130909.0909 | 132000 | [25 empty] | Total Over 18 | 12772 |  | Total Over 18 | 346 | 13118
| 31.87% | 26.96% | 20.4% | 1.665% | 6.376% | 2.112% | 10.6% | 100% | RT Packaged | 5194.4444 | 1% |  |  | 20 |  | Sold | 5194.4444 | 4587.7778 | 4685.5556 | 4861.1111 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | [17 empty] | Total Heat Pump | 119713 |  | Total Cooling Only | 5719 | 125432 |  | 1879786.5
2003 | 109577 | 118407 | 76497 | 7872 | 25309 | 7887 | 53495 | 399044 | [7 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 98% | 95% | 90% | 85% | 80% | 75% | 70% | 62% | 56% | 50% | 44% | 38% | 32% | 26% | 20% | [19 empty] | Total Outdoor Units |  | 125432 |  |  | 14.9865
| 27.46% | 29.67% | 19.17% | 1.973% | 6.342% | 1.976% | 13.41% | 100% | [7 empty] | 68336.8889 | 5194.4444 | 4587.7778 | 4685.5556 | 4861.1111 | 4800 | 4704 | 4560 | 4320 | 4080 | 3840 | 3600 | 3360 | 2976 | 2688 | 2400 | 2112 | 1824 | 1536 | 1248 | 960 | [16 empty] | RT Packaged
| 318531 | 295160 | 210248 | 18787 | 67107 | 21734 | 122977 | 1054594 | Evaporative Coolers | 70000 | -3% |  |  | 13 |  |  | 70000 | 72100 | 74263 | 76490.89 | 78785.6167 | 81149.1852 | 83583.6608 | 86091.1706 | 88673.9057 | 91334.1229 | 94074.1466 | 96896.371 | [24 empty] | Up to 7.5 | 3 | Up to 7.5 | 0 | 3 | 7.5 | 22.5
Av. | 30.2% | 27.99% | 19.94% | 1.781% | 6.363% | 2.061% | 11.66% | 100% | [8 empty] | 100% | 100% | 100% | 96% | 92% | 88% | 84% | 80% | 76% | 70% | 65% | 60% | [24 empty] | >7.5 to 10 | 66 | >7.5 to 10 | 4 | 70 | 10 | 700
[16 empty] | 823383.5884 | 70000 | 72100 | 74263 | 73431.2544 | 72482.7674 | 71411.283 | 70210.275 | 68872.9365 | 67392.1683 | 63933.886 | 61148.1953 | 58137.8226 | [24 empty] | >10 to 12.5 | 126 | >10 to 12.5 | 6 | 132 | 12.5 | 1650
[9 empty] | Gas Ducted Heaters | 69130 | 6% |  |  | 15 |  | Sold | 65491.6872 | 61784.6105 | 58287.3684 | 59930.5263 | 55855.7895 | 48658.9474 | 52242.1053 | 51163.1579 | 49781.7526 | 48437.6453 | 47129.8289 | 45857.3235 | 44619.1758 | 43414.458 | 42242.2677 | 41101.7264 | 39991.9798 | 38912.1964 | 37861.5671 | 36839.3048 | [16 empty] | >12.5 to 15.5 | 199 | >12.5 to 15.5 | 125 | 324 | 15.5 | 5022
[16 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 100% | 97.5% | 95% | 90% | 80% | 70% | 60% | 50% | 40% | 30% | 25% | 20% | 15% | 10% | 5% | [16 empty] | >15.5 to 18 | 279 | >15.5 to 18 | 29 | 308 | 18 | 5544
[16 empty] | 675695.7802 | 65491.6872 | 61784.6105 | 58287.3684 | 59930.5263 | 55855.7895 | 48658.9474 | 50936.0526 | 48605 | 44803.5774 | 38750.1162 | 32990.8802 | 27514.3941 | 22309.5879 | 17365.7832 | 12672.6803 | 10275.4316 | 7998.396 | 5836.8295 | 3786.1567 | 1841.9652 | [16 empty] | Total Up to 18 | 673 | Total Up to 18 | 164 | 837
[9 empty] | Chillers > & = 530 kW | 415 | 3% |  |  | 25 |  |  | 415 | 402.55 | 390.4735 | 378.7593 | 367.3965 | 356.3746 | 345.6834 | 335.3129 | 325.2535 | 315.4959 | 306.031 | 296.8501 | 287.9446 | 279.3062 | 270.9271 | 262.7992 | 254.9153 | 247.2678 | 239.8498 | 232.6543 | 225.6747 | 218.9044 | 212.3373 | 205.9672 | 199.7881 | 193.7945 | 187.9807 | 182.3412 | 176.871 | 171.5649 | 166.4179 | 161.4254 | 156.5826 | 151.8852 | 147.3286 |  | >18 to 25 | 517 | > 18 to 25 | 68 | 585 | 25 | 14625
[16 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.5% | 95% | 90% | 85% | 80% | 77% | 74% | 71% | 0.68 | 0.65 | 0.62 | 0.59 | 0.56 | 0.53 | 0.5 | 0.47 | 0.44 | 0.41 | 0.38 | 0.35 | 0.3 | 0.25 | 0.2 | 0.15 | 0.1 |  | >25 to 30 | 480 | >25 to 30 | 39 | 519 | 30 | 15570
[16 empty] | 6938.8303 | 415 | 402.55 | 390.4735 | 378.7593 | 367.3965 | 356.3746 | 345.6834 | 335.3129 | 325.2535 | 315.4959 | 298.3802 | 282.0076 | 259.1501 | 237.4103 | 216.7416 | 202.3554 | 188.6373 | 175.5601 | 163.0978 | 151.2253 | 139.9183 | 129.1536 | 118.9089 | 109.1626 | 99.8941 | 91.0834 | 82.7115 | 74.7599 | 67.211 | 60.0477 | 49.9254 | 40.3563 | 31.3165 | 22.7828 | 14.7329 |  | >30 to 37.5 | 374 | >30 to 37.5 | 35 | 409 | 37.5 | 15337.5
[9 empty] | Chillers < 530 kW | 192 | 3% |  |  | 25 |  |  | 192 | 186.24 | 180.6528 | 175.2332 | 169.9762 | 164.8769 | 159.9306 | 155.1327 | 150.4787 | 145.9644 | 141.5854 | 137.3379 | 133.2177 | 129.2212 | 125.3446 | 121.5842 | 117.9367 | 114.3986 | 110.9666 | 107.6376 | 104.4085 | 101.2763 | 98.238 | 95.2908 | 92.4321 | [11 empty] | >37.5 to 45 | 356 | >37.5 to 45 | 33 | 389 | 45 | 17505
[16 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.5% | 95% | 90% | 85% | 80% | 77% | 74% | 71% | 68% | 65% | 60% | 50% | 40% | 30% | 20% | [11 empty] | >45 to 65 | 680 | >45 to 65 | 76 | 756 | 65 | 49140
[16 empty] | 2886.2019 | 192 | 186.24 | 180.6528 | 175.2332 | 169.9762 | 164.8769 | 159.9306 | 155.1327 | 150.4787 | 145.9644 | 138.0458 | 130.471 | 119.896 | 109.838 | 100.2757 | 93.6199 | 87.2732 | 81.223 | 75.4573 | 69.9645 | 62.6451 | 50.6381 | 39.2952 | 28.5872 | 18.4864 | [11 empty] | >65 to 77.5 | 208 | >65 to 77.5 | 4 | 212 | 77.5 | 16430
[9 empty] | Precision Control A/C |  | 3% |  |  | 20 |  |  | 960 | 931.2 | 903.264 | 876.1661 | 849.8811 | 824.3847 | 799.6531 | 775.6635 | 752.3936 | 729.8218 | 707.9272 | 686.6893 | 666.0887 | 646.106 | 626.7228 | 607.9211 | 589.6835 | 571.993 | 554.8332 | 538.1882 | [16 empty] | >77.5 to 90 | 169 | >77.5 to 90 | 21 | 190 | 90 | 17100
[16 empty] | % in Service | 100% | 100% | 100% | 100% | 100% | 98% | 95% | 90% | 85% | 80% | 75% | 70% | 62% | 56% | 50% | 44% | 38% | 32% | 26% | 20% | [15 empty] | >90 to 120 | 235 | >90 to 120 | 25 | 260 | 120 | 31200
[16 empty] | 11035.8486 | 960 | 931.2 | 903.264 | 876.1661 | 849.8811 | 807.897 | 759.6705 | 698.0972 | 639.5346 | 583.8575 | 530.9454 | 480.6825 | 412.975 | 361.8194 | 313.3614 | 267.4853 | 224.0797 | 183.0378 | 144.2566 | 107.6376 | [15 empty] | >120 to 160 | 42 | >120 to 160 | 5 | 47 | 160 | 7520
[52 empty] | Over 160 | 13 | Over 160 | 0 | 13 | 250 | 3250
[52 empty] | Total Over 18 | 3074 | Total Over 18 | 306 | 3380
[10 empty] | ABS Import Data | [41 empty] | Total Heat Pump | 3747 | Total Cooling Only | 470 | 4217 |  | 158646
[10 empty] | Year | Volume Units | Value $ | Av. Value | Split Systems | % | VRV | % | Wall Mounted | Ratio Split/Wall | % | Window | % | Total | Total | [30 empty] | 4217 |  |  | 37.6206
[10 empty] | 1997 | 231800 | 114231.044 | 492.8 | 27000 | 11.65% | 0 | 0% | 81000 | 3 | 34.94% | 123800 | 53.41% | 231803.4659 | 231803 | 1997 | 231800 | [25 empty] | Gas Ducted Heaters
[10 empty] | 1998 | 323556 | 171595.791 | 530.3434 | 32000 | 13.8% | 0 | 0% | 96000 | 3 | 29.67% | 195556 | 60.44% | 323559.4347 | 323559 | 1998 | 323556 | [26 empty] | Up to 15Kw | 9114 | 15 | 136710
[10 empty] | 1999 | 299714 | 157234.88 | 524.6164 | 37000 | 15.96% | 0 | 0% | 111000 | 3 | 37.03% | 151714 | 50.62% | 299717.53 | 299717 | 1999 | 299714 | [26 empty] | >15 to 22Kw | 30111 | 22 | 662442
[10 empty] | 2000 | 269882 | 158150.684 | 585.9994 | 42000 | 18.12% | 100 | 0.04314% | 126000 | 3 | 46.67% | 101882 | 37.74% | 269985.6483 | 269985 | 2000 | 269882 | [26 empty] | >22 to 29Kw | 6220 | 26 | 161720
[10 empty] | 2001 | 364527 | 207059.642 | 568.0228 | 47000 | 20.28% | 405 | 0.1747% | 141000 | 3 | 38.64% | 176527 | 48.37% | 364935.5909 | 364935 | 2001 | 364527 | [27 empty] | Over 29Kw | 11089 | 33 | 365937
[10 empty] | 2002 | 549288 | 243769.573 | 443.7919 | 52000 | 22.43% | 579 | 0.2498% | 286000 | 5.5 | 52.01% | 211288 | 38.42% | 549873.2469 | 549872.5 | 2002 | 549288 | [27 empty] | Total Standard Plus Condensing | 56534 |  | 365937
[10 empty] | 2003 | 822777 | 334037.265 | 405.9876 | 57217 | 24.68% | 827 | 0.3568% | 443305.8963 | 7.7478 | 53.82% | 322254.1037 | 39.13% | 823612.5364 | 823611.7478 | 2003 | 822777 | [30 empty] | 6.4729
[10 empty] | 2004 | 1165739 | 423783.915 | 363.5324 | 92959 | 40.1% | 1181 | 0.5095% | 555869.4625 | 5.9797 | 47.64% | 516910.5375 | 44.3% | 1166920 | 1166925.9797 | 2004 | 1165739 | [26 empty] | Wall Hung Splits
[10 empty] | 2005 | 1013727 | 374046.486 | 368.9815 | 88476 | 38.17% | 2250 | 0.9707% | 697015 | 7.878 | 68.6% | 147807 | 14.55% | 935548 | 1015984.878 | 2005 | 1013727 | [26 empty] | Up to 2 | 2880 | 1039 | 3919 | 7838
[10 empty] | 2006 | 1061758 | 453944.528 | 427.5405 | 103752 | 44.76% | 3000 | 1.294% | 874000 | 8.4239 | 76.79% | 166807 | 14.66% | 1147568.6524 | 1138157.4239 | 2006 | 1061758 | [26 empty] | >2.to 3 | 62836 | 17709 | 80545 | 241635
[53 empty] | >3 to 4 | 53884 | 8527 | 62411 | 249644
[53 empty] | >4 to 4.6 | 3714 | 294 | 4008 | 18436.8
[53 empty] | >4.6 to 5.4 | 37903 | 4476 | 42379 | 228846.6
[53 empty] | >5.4 to 7.5 | 140445 | 12636 | 153081 | 1148107.5
[53 empty] | >7.5 to 18 | 46164 | 6116 | 52280 | 470520
[53 empty] | Over 18 | 421 | 0 | 421 | 7578
[54 empty] | 348247 | 50797 | 399044 | 2372605.9
5.9457
[17 empty] | 2005 | 697015 | 228236
[17 empty] | 2006 | 874000 | 157397
Note on L32: Annual rate for Commercial A/C of 425 p.a. based on the following: - 2005/6, 488 chillers sold over 528kW - Historic Rate, consistently been around 400 chillers p.a. - MEPS 2004 estimate of installed base 6,000 to 7,000 units - Annual rate of 425 p.a. calculates an existing stock of 7,100 which is equiv. to av. MEPS estimate plus 3% growth rate.
Note on T18: DEH Import Data 2006 = 166,807 2005 = 147,987
Note on T51: Informark 2003 WHS = 399,044 Assume 90% Participation rate = 90% Estimate units sold = 443,382
Note on U18: Value was 516,910, revised down to 316,910 as was not statistically consitent.
Note on V13: Informark 2003 WHS = 399,044 Assume 90% Participation rate = 90% Estimate units sold = 443,382
Note on V19: Kelvinator plant stopped mfg window units around this time
Note on W52: Possible anomally, however, difference b/n wall or window is less significant
Note on W53: DEH Import Data 2006 = 166,807 2005 = 147,987
Note on AH14: Estimate quoted by K Finn via Email Air report
Note on AH20: Estimate quoted by K Finn via Email Air report
ABS Import Data Obtained (mix of old & new codes due to changes)
Obtained data on new codes 8415100037, 8415100038, 8415100039, 8415100049 includes Window or wall type split systems (all kW sizes covered by codes) for Years 2006, 2005, 2004, 2003, 2002
Plus data on old codes 8415820061, Air Conditioning incorporating a refrigerating unit 8415100045, 8415100046, 8415100047, 8415100048 includes Window/wall type air cond. machines, self-contained (all kW sizes covered by codes) for Years 2001, 2000, 1999, 1998, 1997
Import code descriptors & history is listed below:-
Current 10 digit codes and their descriptors:
8415100037 Window or wall-type self contained or split system air conditioning machines less than 3 kW
8415100038 Window or wall-type self contained or split system air conditioning machines 3 kW or more but less than 4 kW
8415100039 Window or wall-type self contained or split system air conditioning machines 4 kW or more but less than 5 kW
8415100049 Window or wall-type self contained or split system air conditioning machines 5 kW or more
Code history:
8415100037 This code commenced on 1/1/2002; the previous codes were 8415820061 and 8415100045, both of which ceased on 31/12/2006
8415100038 This code commenced on 1/1/2002; the previous codes were 8415820061 and 8415100046, both of which ceased on 31/12/2006
8415100039 This code commenced on 1/1/2002; the previous codes were 8415820061 and 8415100047, both of which ceased on 31/12/2006
8415100049 This code commenced on 1/1/2002; the previous codes were 8415820061 and 8415100048, both of which ceased on 31/12/2006
Previous 10 digit codes and their descriptors:
8415820061 Air conditioning machines incorporating a refrigerating unit (excl. those for use in motor vehicles, window or wall types, self-contained, and those incorporating a refrigerating unit and a valve for reversal of the cooling/heat cycle)
8415100045 Window/wall type air cond. machines, self-contained, not exc 3.0 kW, comprising a motor-driven fan & elements for changing the temp. & humidity (incl those machines in which the humidity cannot be separately regulated)
8415100046 Window/wall type air cond. machines, self-contained, exc 3.0 kW, but not exc 4.0 kW, comprising a motor-driven fan & elements for changing temp. & humid (incl those machines in which the humid cannot be separately regulated)
8415100047 Window/wall type air cond. machines, self-contained, exc 4.0 kW, but not exc 5.0 kW, comprising a motor-driven fan & elements for changing temp. & humidity (incl those machines in which the humid cannot be separately regulated)
8415100048 Window/wall type air cond. machines, self-contained, exc 5.0 kW, comprising a motor-driven fan & elements for changing temp. & humidity (incl those machines in which the humidity cannot be separately regulated)
Existing Stock Calculations & assumptions:
Assumed 100% systems were in service for the nominal warranty period (for domestic applications) then discounted the % in service to a typical life span.
Split Systems (Warranty period: majors = 5 yrs/minors = 3 yrs, used 4 yrs), then discounted to 70% at 10 years & 60% at 12 years)
WHS Systems (Warranty period: majors = 5 yrs/minors = 3 yrs, used 4 yrs), then discounted to 60% at 10 years
Window/Wall (Warranty period: 3 yrs), then discounted to 65% at 10 years & 55% at 12 years)
Evaporative Coolers (Warranty period: 3 yrs), then discounted to 70% at 10 years & 60% at 12 years)
Existing Stock can be subjective as units can still be installed, however not operated or only used occasionally (a good example of this is a wall unit replaced by a WHS System, wall units are rarely replaced in a domestic application as it involves re-plastering & filling the external hole at a cost of $500 to $1,000).
There is limited research in this area, however one reference is as follows:
Status of AC in Australia, EES, 2005 pp12 Studies undertaken by Test Research in 1995 indicate the av. age of AC's to be 8 years, with the av, retirement age of 12 to 18 years (depending on installation, type), which was broadly consistent with BIS Shrapnel Data collected in 2004. Until a more comprehensive study is undertaken intuition from industry Product Managers & Service Managers is the best guide.
WHS Systems (Warranty period: majors = 5 yrs/minors = 3 yrs, used 4 yrs), then discounted to 60% at 10 years
Window/Wall (Warranty period: 3 yrs), then discounted to 65% at 10 years & 55% at 12 years)
Evaporative Coolers (Warranty period: 3 yrs), then discounted to 70% at 10 years & 60% at 12 yrs)

## Split Systems-Industry Data
Split System Sales
Product Type | Year | Av. Size (kW) | Quantity (Units) | Growth (%) | Value ($000) | Av. Value | Est. Participation Rate | Est. Quantity Sold (Units) | Est. Imported | Est. Imported (Units)
Indoor Unit | 2006 |  | 136830 |  | 146626 | 1071.5925
Outdoor Unit |  |  | 133395 | 14.58% | 278753 | 2090 | 90% | 148216.6667 | 70% | 103751.6667
Split System Total |  |  |  |  | 425379 | 3188.8676
Indoor Unit | 2005 |  | 117670 |  | 121770 | 1034.8432
Outdoor Unit |  |  | 116416 | -7.188% | 238923 | 2052 | 90% | 129351.1111 | 68.4% | 88476.16
Split System Total |  |  |  |  | 360695 | 3098.3284
Indoor Unit | 2004 | - | 127470 |  | 131969 | 1035.2946
Outdoor Unit |  | - | 125432 | 58.33% | 260918 | 2080 | 90% | 139368.8889 | 66.7% | 92959.0489
Split System Total |  | 15 | - |  | 392887 | 3132.2709
Indoor Unit | 2003 |  | - |  | - | -
Outdoor Unit |  |  | 79224 |  | - | - | 90% | 88026.6667 | 65% | 57217.3333
Split System Total |  |  | - |  | 254485 | 3212
Notes & Assumptions:
Unit volumes & values are for suppliers/manufacturers & do not include retail/wholesalers
Av. kW size is weight value based on unit volumes
Split systems includes ducted, cassette, console & under ceiling
Applications include residential & light commercial
100% Powered by Electricity
Participants:
Temperzone
Carrier
ECP
Mitsubishi Electric
Hitachi Australia
LG Electronics
Panasonic
Fujitsu General
Mitsubishi Heavy Industries
Trane
Lennox
Samsung
Actron Air
Daikin
Note on A2: The statistical Data was collected via industry sources & used in conjunction with import data from DEH & Import statistics from ABS. Industry gain accurate information as follows: - Market leaders with a significant share & years of experience have a good understanding of market sizes/details by product category - Unit volumes & typical sizes are estimated at industry gatherings such as MEPS committees - Several product categories are recorded by Informark, this information is only available to members that subscribe, participants can estimate total market data by estimating participation rate
Note on C2: Watts relates to nominal cooling capacity (ARI 26.1oC db/19.4oC wb air on & 35oC ambient)
Note on F2: Value ($000) p.a. is calculated by multiplying Av. Value (wholesale) x Quantity (units) p.a. For better indication of the commercial value, multiply retail price by 2 to 4 times for total installed price (depending on technology & complexity of application) Eg 5kW Wall Mounted Hitachi Inverter Split = $1050/0.8 x 2 = $2,625.00 fully installed incl. GST Eg 15kW split ducted system $3189/0.75 x 2.5 = $10,630.00 fully installed incl. GST More complex installations use higher multipliers
Note on G2: Av. value is at wholesale (equipment only, not installed) add 20 to 30% GM for retail

## RT Packaged-Industry Data
Product Type | Year | Av. Size (kW) | Quantity (Units) | Growth (%) | Value ($000) | Growth (%) | Av. Value | Est. Participation Rate | Est. Imported | Est. Av. Life (Yrs)
RT Packaged Systems | 2006 |  | 4675 | 13.22% | 38576 | 10.78% | 8252 | 90% | 25% | 25
| 2005 |  | 4129 | -2.087% | 34823 | -2.152% | 8471
| 2004 | 47.6 | 4217 | -3.611% | 35589 | -9.491% | 8440
| 2003 |  | 4375 |  | 39321 |  | 8988
Notes & Assumptions:
Unit volumes & values are for suppliers/manufacturers & do not include retail/wholesalers
Av. kW size is weight value based on unit volumes
Over 95% of applications are commercial
95% Powered by Electricity & 5% Powered by Gas
Participants:
Temperzone
Carrier
ECP
Mitsubishi Electric
Hitachi Australia
LG Electronics
Mitsubishi Heavy Industries
Trane
Lennox
Actron Air
Daikin

## WHS System-Industry Data
Product Type | Year | Av. Size (kW) | Quantity (Units) | Growth (%) | Value ($000) | Growth (%) | Av. Value | Est. Participation Rate | Est. Imported
Wall Mounted | 2006 | 6 | 655500 |  |  |  |  | 75%
Notes & Assumptions:
Unit volumes & values are for suppliers/manufacturers & do not include retail/wholesalers
Av. kW size is weight value based on unit volumes
100% Powered by Electricity
Majority sold in 2006/7 were inverter, except Qld
Large majority are reverse cycle
Key Participants:
Electrolux
Carrier
ECP
Mitsubishi Electric
Hitachi Australia
LG Electronics
Panasonic
Fujitsu General
Mitsubishi Heavy Industries
Trane
Lennox
Samsung
Actron Air
Daikin
NEC
Sharp
Sanyo
Cooline
Over 100 Brands in split market

## Gas Ducted-Industry Data
Product Type | Year | Av. Size (kW) | Quantity (Units) | Growth (%) | Value ($000) | Growth (%) | Av. Value | Est. Participation Rate | Est. Imported | Est. Av. Life (Yrs)
| 2006 |  | 62217.1028
| 2005 |  | 58695.38
Gas Ducted Heaters | 2004 | 23.5 | 55373 | -2.742% |  |  |  | 90% | 15% | 15
| 2003 |  | 56934 | 7.295%
| 2002 |  | 53063 | 14.79% |  |  |  | - | - | -
| 2001 |  | 46226 | -6.859%
| 2000 |  | 49630 | 2.109%
| 1999 |  | 48605
Notes & Assumptions:
Unit volumes & values are for suppliers/manufacturers & do not include retail/wholesalers
Av. kW size is weight value based on unit volumes
Over 90% of applications domestic
100% Powered by Natural Gas or LPG
Participants:
Climate Technologies - Vulcan
Brivis
Seely - Breamar
Lennox
Stadt (in liquidation)

## Greenhouse Emission Factors
AGO Factors and Methods Workbook, Department of the Environment and Heritage, December 2006
Table 3: Fuel combustion emission factors (Transport Fuels)
| Fuel | Energy content | Emission factor for scope 1 |  | Emission factor for scope 3 |  | Full fuel cycle emission factor
|  |  | (direct / point source EF for combustion emissions |  | (indirect EF for fuel extraction emissions) |  | (= EF for scope 1 + scope 2)
|  | A | B | C | D | E | F | G
|  | GJ/kL | kg CO2-e/GJ | t CO2-e/kL | kg CO2-e/GJ | t CO2-e/kL | kg CO2-e/GJ | t CO2-e/kL
| Automotive gasoline | 34.2 | 69.4 | 2.4 | 7.8 | 0.3 | 77.2 | 2.6
(petrol)
| Automotive diesel oil | 38.6 | 69.8 | 2.7 | 7.8 | 0.3 | 77.6 | 3
(diesel)
| Aviation gasoline | 33.1 | 66.7 | 2.2 | 7.8 | 0.3 | 74.5 | 2.5
| Aviation turbine | 36.8 | 70.7 | 2.6 | 7.8 | 0.3 | 78.5 | 2.9
| Fuel oil | 40.8 | 74.3 | 3 | 7.8 | 0.3 | 82.1 | 3.3
| LPG | 26.2 | 61.5 | 1.6 | 7.8 | 0.2 | 69.3 | 1.8
Biofuels a
| E-10 molasses | 32.9 | 62.4 | 2.1 | 6 | 0.2 | 68.5 | 2.3
| E-10 wheat starch | 32.9 | 62.4 | 2.1 | 7.3 | 0.2 | 69.7 | 2.4
| BD 100 (canola) | 34.7 | 0.8 | 0 | 59 | 2.1 | 59.8 | 2.1
| BD100 (tallow) | 34.7 | 0.8 | 0 | 54.3 | 1.9 | 55.1 | 1.9
| BD100 (waste oil) | 34.7 | 0.8 | 0 | 7.4 | 0.3 | 8.1 | 0.3
| BD20 (canola) | 37.8 | 54.7 | 2.1 | 16.1 | 0.6 | 70.9 | 2.7
| BD20 (tallow) | 37.8 | 54.7 | 2.1 | 16.9 | 0.6 | 71.6 | 2.7
| BD20 (waste oil) | 37.8 | 54.7 | 2.1 | 7.1 | 0.3 | 61.8 | 2.3
|  | GJ/m3 | kg CO2-e/GJ | t CO2-e/m3 | kg CO2-e/GJ | t CO2-e/m3 | kg CO2-e/GJ | t CO2-e/m3
| Natural gas b (LDV c) | 0.0395 | 57.2 | 0.0023 | 11.4 | 0.00045 | 68.6 | 0.0027
| Natural gas b (HDV c) | 0.0395 | 53.8 | 0.0021 | 11.4 | 0.00045 | 65.2 | 0.0026
Notes: * All emission factors incorporate relevant oxidation factors (sourced from the AGO’s National Inventory Report).
Respective Scope 1 CO2 factors are available from the AGO’s National Inventory Report.
a AGO estimates, derived from ‘Appropriateness of a 350 Million Litre Biofuels Target’, December 2003, CSIRO, ABARE,
BTRE. The emission factors reported here are default factors - to be used in the absence of better data on emissions that may
result, for example, on actual production methods employed. b. The emission factors for natural gas engines are indicative
only. From AGO experience with the Alternative Fuels Conversion Programme, the AGO has discovered that many natural gas
engines, whether dual fuel or dedicated, emit significant amounts of unburnt fuel to the atmosphere. This level of methane is
dependent on a range of factors and varies from system to system. An accurate emissions factor therefore requires measurement
of at least CO2 and CH4 for each engine type. c. LDV stands for Light Duty Vehicles, e.g. forklifts, and HDV stands for Heavy
Duty Vehicles, e.g. buses.
Table 18: Emission factors for consumption of purchased electricity—for end users (not distributors)
| State | EF for scope 2 |  | EF for scope 3 |  | Full fuel cycle EF
|  | Direct / point source EF for combustion emissions |  | Indirect EF for fuel extraction and line loss (T&D) emissions |  | (= EF for scope 2 + scope 3)
|  | A | B | C | D | E | F
|  | kg CO2-e/ | kg CO2-e/ | kg CO2-e/ | kg CO2-e/ | kg CO2-e/ | kg CO2-e/
|  | kWh | GJ | kWh | GJ | kWh | GJ
| NSW & ACT | 0.893 | 248 | 0.176 | 49 | 1.068 | 297
| VIC | 1.239 | 344 | 0.086 | 24 | 1.325 | 368
| QLD | 0.903 | 251 | 0.143 | 40 | 1.046 | 291
| SA | 0.865 | 240 | 0.177 | 49 | 1.042 | 290
| WA (SWIS) | 0.84 | 233 | 0.096 | 27 | 0.936 | 260
| TAS | 0.05 | 14 | 0.01 | 3 | 0.06 | 17
| NT | 0.682 | 189 | 0.034 | 9 | 0.716 | 199
Notes: a The emission factors should be applied to the amount of electricity actually consumed (i.e. the amount shown on the
electricity bill). A technical explanation of the definitions and units of these factors are provided in the box on pages 14 and
15. b kg CO2-e/GJ is the same as kt CO2-e/PJ and Gg CO2-e/PJ. Transmission and distribution network operators should
use the EFs in Appendix 6.
Table 23: Global Warming Potentials
| Gas | Chemical formula | IPCC 1996 Global
Warming Potential
| Carbon dioxide | CO2 | 1
| Methane | CH4 | 21
| Nitrous oxide | N2O | 310
Hydrofluorocarbons HFCs
| HFC-23 | CHF3 | 11700
| HFC-32 | CH2F2 | 650
| HFC-41 | CH3F | 150
| HFC-43-10mee | C5H2F10 | 1300
| HFC-125 | C2HF5 | 2800
| HFC-134 | C2H2F4 (CHF2CHF2) | 1000
| HFC-134a | C2H2F4 (CH2FCF3) | 1300
| HFC-143 | C2H3F3 (CHF2CH2F) | 300
| HFC-143a | C2H3F3 (CF3CH3) | 3800
| HFC-152a | C2H4F2 (CH3CHF2) | 140
| HFC-227ea | C3HF7 | 2900
| HFC-236fa | C3H2F6 | 6300
| HFC-245ca | C3H3F5 | 560
Hydrofluoroethers (HFEs)
| HFE-7100 | C4F9OCH3 | 500
| HFE-7200 | C4F9OC2H5 | 100
Perfluorocarbons PFCs
| Perfluoromethane (tetrafluoromethane) | CF4 | 6500
| Perfluoroethane (hexafluoroethane) | C2F6 | 9200
| Perfluoropropane | C3F8 | 7000
| Perfluorobutane | C4F10 | 7000
| Perfluorocyclobutane | c-C4F8 | 8700
| Perfluoropentane | C5F12 | 7500
| Perfluorohexane | C6F14 | 7400
| Sulphur hexafluoride | SF6 | 23900
Indirect gases
| Carbon monoxide | CO | not applicable
| Oxides of nitrogen | NOx | not applicable
| Non-methane volatile organic compounds | various | not applicable
(NMVOCs)

## Areas of Improvement
Areas of Improvement to Enhance Accuracy & Fill Data Gaps
Survey Daikin, Fujitsu, etc. % of Commercial AC to domestic on WHS Systems & Split Sytems.
Industry # 's for Evaporative coolers (annual sales, existing stock & split by region).
Effective operating time for Chillers for Commercial AC, Food Chain & Industrial Applications (used in Energy Calculation).
Seasonal operating times used for calculating domestic operating hours are based on data quoted on www.energyrating.gov.au calculator, originally sourced based on EES estimates & ABS data (used in Energy Calculation for Domestic AC)
Data gap in Industrial (Ammonia) Refrigeration, requires further investigation in this segment (nominated best estimate to complete analysis).
Confirm data on self contained merchandising equipment & complete energy calculation.
Obtain further data on Pubs, Clubs, Pubs/Clubs/Convenience Stores/Take Away Food & complete energy calculation (taking into account self contained merchandising equipment & coolrooms).
Quotations to confirm av. consumer prices for residential applications (used to calculate Consumer Spend).
More actual energy consumption data from Industry or Energy companies.