207

supervising scientist  report

Investigation into the environmental impacts of the leach tank failure at Ranger uranium mine, December 2013

Supervising Scientist

It is Supervising Scientist Division policy for reports in the SSR series to be reviewed as part of the publications process. This Supervising Scientist Report has been reviewed internally by senior staff.

Editor

Supervising Scientist – Supervising Scientist Division, GPO Box 461, Darwin NT 0801, Australia.

This report should be cited as follows:

Supervising Scientist 2014. Final Report: Investigation into the environmental impacts of the leach tank failure at Ranger uranium mine, December 2013. Supervising Scientist Report 207, Supervising Scientist, Darwin NT.

The Supervising Scientist is part of the Australian Government Department of the Environment

© Copyright Commonwealth of Australia, 2014

SSR207 is licensed by the Commonwealth of Australia for use under a Creative Commons By Attribution 3.0 Australia licence with the exception of the Coat of Arms of the Commonwealth of Australia, the logo of the agency responsible for publishing the report, content supplied by third parties, and any images depicting people. For licence conditions see: http://creativecommons.org/licenses/by/3.0/au/

ISSN  1325-1554 (online)

ISBN  978-1-921069-24-6

Internet: environment.gov.au/ssd/publications

The views and opinions expressed in this publication are those of the authors and do not necessarily reflect those of the Australian Government or the Minister for the Environment.

While reasonable efforts have been made to ensure that the contents of this publication are factually correct, the Commonwealth does not accept responsibility for the accuracy or completeness of the contents, and shall not be liable for any loss or damage that may be occasioned directly or indirectly through the use of, or reliance on, the contents of this publication.

Contents

Executive summary	1

1  Introduction	3

1.1  Scope of investigation	3

1.2  Ranger uranium mine	3

1.2.1  Overview of Ranger water classes	3

1.3  Legislative framework	6

1.4  The Supervising Scientist monitoring program	7

2  Description of the incident	9

2.1  Incident summary	9

2.2  Ranger mine Leach Tank Incident Task Force	9

2.3  Leach slurry properties	10

2.4  Spatial extent of the spill	10

2.5  Cleanup operation	13

3  Supervising Scientist Division Response	14

3.1  Initial response	14

3.1.1  SSD initial site inspection	14

3.1.2  Supervising Scientist’s inspection	15

3.1.3  Routine Periodic Inspection	15

3.2  Surface Water	18

3.2.1  Onsite surface water	18

3.2.2  Offsite surface water	23

3.3  Groundwater	24

3.3.1  Soil profiling	24

3.3.2  Groundwater impact assessment by Geoscience Australia	25

3.4  Radiation exposure	27

3.4.1  Gamma dose rate measurements on site	27

3.4.2  Radionuclide analyses in the spilled slurry	28

4  Data analysis and discussion	31

4.1  Surface Water	31

4.1.1  Surface water quality assurance/quality control	31

4.1.2  Onsite surface water	31

4.1.3  Offsite surface water	48

4.2  Ground Water	55

4.2.1  Onsite soil profiling	55

4.2.2  Groundwater impact assessment by Geoscience Australia	64

4.3  Radiation Exposure	73

4.3.1  Initial gamma dose rate measurements	73

4.3.2  Assessment of radiation dose from the spilled material to ERA staff and contractors	73

4.3.3  Assessment of radiological impacts to the public	79

5  Conclusions	85

5.1  Surface water	85

5.2  Groundwater and soils	86

5.3  Radiation exposure	86

6  Recommendations	88

References	89

Tables

Table 1.1  Indicative Water Quality of Water Classes (from ERA 2013)	6

Table 2.1  Slurry material and leach tank details	10

Table 2.2  Slurry chemical properties	10

Table 2.3  Estimated spill area by groundcover type (ERA data)	11

Table 2.4  Slurry samples received for analysis	28

Table 4.1  Relative Percent Difference (RPD) in the soil concentration between the exposed and the control soils for elements that were elevated in the exposed soil.	44

Table 4.2  Corrected key filterable analyte concentrations in runoff from Zone 1	45

Table 4.3  Key filterable analyte concentrations measured in pooled rainfall from Zone 2	46

Table 4.4  Key analyte concentrations measured in pooled rainfall from Zone 3	47

Table 4.5  Results of ANOVA testing comparing Magela upstream-downstream difference values for mean snail egg number for different ‘before versus after’ wet season scenarios	55

Table 4.6  Mean exposed water extractable concentrations for elements that were elevated in exposed soils compared to control soils, along with the mean dissolved concentrations measured in the slurry and the RP2 indicative water quality concentrations, where available	63

Table 4.7  Results of radionuclide analysis in the slurry samples	74

Table 4.8  Inhalation dose coefficients for radon decay products (RDP) and long lived alpha activity (LLAA) assuming an activity mean aerodynamic diameter (AMAD) of 5 µm and 0% radon retention in the crushed and leached material	76

Table 4.9  Breathing rates (m3 hr-1) for a male adult and worker for different physical activities	76

Table 4.10  Dose rates [µSv hr-1] estimated for workers involved in the cleanup	78

Table 4.11  Mean annual doses (in mSv) received by workers in the Processing Production working group in 2013 (ERA 2014) and estimated doses (in mSv) received during the cleanup operation	78

Table 4.12  Mean and standard deviation of average hourly radon progeny concentrations in air at Jabiru Town and Jabiru East in the two weeks before and two weeks after the incident	83

Figures

Figure 1.1  The Alligator Rivers Region	4

Figure 1.2  Water class catchments on the Ranger mine site (ERA 2013)	5

Figure 1.3  Ranger minesite	8

Figure 2.1  Collapsed Leach Tank 1	9

Figure 2.2  Ranger minesite showing spatial extent of the slurry spill	11

Figure 2.3  Slurry spill area by groundcover type. ERA data	12

Figure 2.4  Leach tank bund following the failure of Leach Tank 1	13

Figure 2.5  Scraped grass verge following cleanup. Grass cover adjacent to the road verge was removed during clean up	13

Figure 3.1  Looking south east at the failed tank from the end of the slurry flow	14

Figure 3.2  Lateral spread of the slurry in low lying areas	14

Figure 3.3  Containment bunding between RP2 and leach tanks	16

Figure 3.4  Classification of impact zones for wash down purposes	17

Figure 3.5  Example of drain blockage	17

Figure 3.6  Sample locations for soil scrapes	19

Figure 3.7  Sample locations for Zone 1 clearance	20

Figure 3.8  Sample locations for Zone 2 clearance	21

Figure 3.9  Excavated area within Zone 3	22

Figure 3.10  Excavated area within Zone 3	22

Figure 3.11  Sample location for Zone 3 clearance	22

Figure 3.12  Location of Magela Creek Upstream (MCUGT) and Magela Creek Downstream (MCDW) monitoring sites	23

Figure 3.13  Location of soil profiles	25

Figure 3.14  Results of the gamma dose rate measurements taken around the perimeter of the spill impacted area and within Zone 1 on 8 December 2013	27

Figure 3.15  Results of the gamma dose rate measurements taken around the perimeter of the spill impacted area and within Zone 1 on 12 December 2013	28

Figure 3.16  Location of the samples collected by ERA in the morning of 7 December 2013	29

Figure 4.1  Continuous Electrical Conductivity (EC) data from RP2 for A) 19 January 2011 to 7 August 2014; B) November 2013 to March 2014; and C) box plots comparing EC in RP2 before (n=25190) and after the incident (n=5841). Data from ERA	32

Figure 4.2  Explanatory diagram of a box plot	33

Figure 4.3  pH data from RP2 for A) 13 December 2011 to 7 July 2014; B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=68) and after the incident (n=36). Data from ERA	34

Figure 4.4  Filterable Magnesium (Mg) data from RP2 for A) 13 December 2011 to 7 July 2014;  B) 9 November 2013 to 11 April 2014; and C) box plots comparing Mg in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA	36

Figure 4.5  Filterable Calcium (Ca) data from RP2 for A) 13 December 2011 to 7 July 2014; B) 9 November 2013 to 11 April 2014; and C) box plots comparing Ca in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA	37

Figure 4.6  Filterable Manganese (Mn) data from RP2 for A) 13 December 2011 to 7 July 2014; B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=61) and after the incident (n=37). Data from SSD and ERA	38

Figure 4.7  Filterable Sulfate (SO4) data from RP2 for A) 13 December 2011 to 7 July 2014; B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA	40

Figure 4.8  Filterable Uranium (U) data from RP2 for A) 13 December 2011 to 7 July 2014; B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=61) and after the incident (n=37). Data from SSD and ERA	41

Figure 4.9  Radium-226 (226Ra) data from RP2 for A) filterable and residual activity concentrations for 1988–2014; B) total activity concentrations for December 2011 to December 2013; and C) box plots comparing EC in RP2 before and after the incident. Data from SSD and ERA (Akber et al. 2011)	43

Figure 4.10  Continuous EC data for Magela Creek from 28 November 2013–27 December 2013. SSD data	48

Figure 4.11  Continuous pH data for Magela Creek from 28 November 2013–30 December 2013 (SSD data). The pH trigger values are provided for information only as these trigger values were determined statistically from historical weekly grab sampling data, and only apply to water quality measured in grab samples	49

Figure 4.12  SSD continuous turbidity data for Magela Creek from 28 November 2013–30 December 2013. The turbidity trigger values are provided for information only as these trigger values were determined statistically from historical weekly grab sampling data, and only apply to water quality measured in grab samples	50

Figure 4.13  SSD uranium concentration data and continuous EC for Magela Creek from  28 November 2013–30 December 2013. SSD data	51

Figure 4.14  SSD manganese concentration data and continuous EC for Magela Creek from  28 November 2013–30 December 2013. SSD data	51

Figure 4.15 SSD magnesium concentration data and continuous EC for Magela Creek for 28 November 2013–30 December 2013	52

Figure 4.16  226Ra in Magela Creek 2001–2014	53

Figure 4.17  Time-series of snail egg production data from toxicity monitoring tests conducted in  Magela Creek. The time of the incident is denoted within the figure by the vertical red line	54

Figure 4.18  Sediment sampling hole 1	56

Figure 4.19   Auger mounted on a bobcat used to drill hole 2	56

Figure 4.20  Sediment sampling hole 3	57

Figure 4.21  Sediment sampling hole 4	57

Figure 4.22  Sediment sampling hole 5	58

Figure 4.23  Depth profiles of radiation levels for holes 1, 3, 4 and 5. Because hole 2 was sampled with an auger, no profile image is available	59

Figure 4.24  Comparison of water extractable concentrations in control and exposed soils at different depths	60

Figure 4.25  Comparison of acid extractable concentrations in control and exposed soils at different depths	61

Figure 4.25  Long-term average of wet season water-level records. Bores with fewer than 100 records have been labelled with the number of records available. Arrows indicate the direction of groundwater flow. Image courtesy of Geoscience Australia	66

Figure 4.26  Long-term average of dry season water-level records. Bores with fewer than 100 records have been labelled with the number of records available. Arrows indicate general direction of groundwater flow. Image courtesy of Geoscience Australia	67

Figure 4.27  Rainfall compared to GC2 discharge from July 2010 to February 2014 (rainfall data from BoM 2014; GC2 discharge volumes supplied by ERA). Image courtesy of Geoscience Australia	68

Figure 4.28  Natural neighbour interpolated surface of average SO4 concentrations in groundwater between 2006 and 2013. Labelled bores are used for more detailed analysis. Image courtesy of Geoscience Australia	70

Figure 4.29  Stiff Diagram from bores 35 and 36 on 15/01/2009 showing Mg/SO4 and Na+K/SO4 water types. (Image courtesy of Geoscience Australia).	71

Figure 4.30  Stiff Diagrams from bores 35 and 36 post-spill composition. Image courtesy of Geoscience Australia	71

Figure 4.31  Effective gamma dose rates for various thicknesses of dried material with an activity concentration of 238U in equilibrium with its decay products of 21.6 Bq g-1	75

Figure 4.32  Dose rate from the inhalation of radon decay products for various thicknesses of dried material with an activity concentration of 238U of 21.6 Bq g-1 in radioactive equilibrium with its decay products. Dose rates were modelled using the ResRad computer code and assuming a worker is standing on top of the spilled material and assuming a low wind speed of < 1 m s-1 and atmospheric stability class A	77

Figure 4.33  Histogram (left) and cumulative probability (right) of long lived alpha activity concentrations measured during the cleanup of the spill	77

Figure 4.34  Uranium-238 decay series showing radon progeny (red) and LLAA radionuclides (brown)	79

Figure 4.35  Frequency histogram of wind direction data from the BoM weather station at Jabiru Airport for the two weeks after the incident (7–20 December 2013). The circumferential axis shows wind direction in ten degree sectors. The radial axis shows the number of half-hourly periods that the wind was from each sector. The blue shaded sector represents the direction of Jabiru Town from the Ranger mine and the red shaded sector represents the direction of Jabiru East from the Ranger mine. A wind direction of 0 indicates still conditions (i.e. no wind)	81

Figure 4.36  Hourly radon progeny monitoring data and hourly rainfall data from two weeks before to two weeks after the incident	82

Figure 4.37  Average hourly radon progeny concentration and average hourly wind speed from for the four week period from two weeks before to two weeks after the incident	82

Figure 4.38  Comparison of average hourly radon progeny concentrations in air for the two weeks before (grey line) and two weeks after (black line) the incident	83

Figure 4.39  LLAA concentrations measured in dust from approximately two weeks before to two weeks after the incident. The dotted lines represent two standard deviations of the measured value based on counting statistics	84

# Executive summary

At 00.54 am on 7 December 2013 Leach Tank 1 at the Energy Resources of Australia Ltd Ranger uranium mine collapsed, spilling approximately 1 400 m3 of slurry containing ground uranium ore, water and sulfuric acid into the processing area. The Supervising Scientist was advised of the incident at 06.20 am on 7 December 2013, with Supervising Scientist Division staff onsite that morning to assess the scale of the incident and begin analysis of the potential environmental impacts.

No one was injured as a result of the incident and the spill remained within the processing area with an unknown quantity of slurry reporting to Retention Pond 2.

A joint Commonwealth/Northern Territory Government Taskforce, with representation from the Supervising Scientist (Australian Government Department of the Environment), the Australian Government Department of Industry, Northern Territory Department of Mines and Energy, Northern Territory WorkSafe, Northern Land Council and the Gundjeihmi Aboriginal Corporation, was established to coordinate the various incident investigations.

The Supervising Scientist’s investigation is confined to the assessment of the potential impacts on human health and the offsite environment, including Kakadu National Park, as a result of the incident. The Supervising Scientist’s investigation does not consider the cause of the leach tank failure, nor does it consider issues related to the condition of the Ranger uranium mine processing facility, as this remains the subject of ongoing investigations by the Northern Territory Department of Mines and Energy and Northern Territory WorkSafe.

In assessing the environmental impacts from this incident, the Supervising Scientist undertook a comprehensive array of monitoring activities which included both onsite and offsite sampling and analysis of surface water, groundwater, radiation and soils. In addition Geoscience Australia was commissioned by the Supervising Scientist to investigate the potential impacts to groundwater as a result of the spill.

It is the conclusion of the Supervising Scientist that the leach tank failure has not resulted in any adverse impacts to human health or the surrounding environment, including Kakadu National Park.

Radiological assessment of both the spill site and personal dosimeters show that additional radiation doses to workers involved in the cleanup activities were low and assessed to be of no concern to human health. No increase in airborne radionuclide concentrations as a result of the incident was detected at the Supervising Scientist monitoring stations in Jabiru town or at Jabiru East.

Chemical and biological monitoring by the Supervising Scientist in Magela Creek did not detect any effects related to the incident. Limited groundwater data available in the area of the spill, and the six week timeframe for Energy Resources of Australia Ltd to commence the requested groundwater monitoring program, restricted the level of groundwater analysis which could be undertaken. However, sufficient information was available to conclude that due to the generally compacted nature of soils in the plant area only a small volume of contaminants may have entered the groundwater and this would not have any significant impact on groundwater quality in the offsite environment.

It is recommended that Energy Resources of Australia Ltd provide the Ranger Minesite Technical Committee with an implementation plan to address the recommendations of the Geoscience Australia report, including:

- an increase in the frequency and density of routine groundwater monitoring in both the plant area and the Corridor Creek region.

- investigate the role of geological structures in groundwater movement to the east of the plant area.

- continue the development and maintenance of a spatial database of groundwater data for the Ranger uranium mine; and

It is recommended that soil contamination investigation works undertaken by Energy Resources of Australia Ltd in 2006 and 2007 be revisited to better inform site closure planning.

# 1  Introduction

## 1.1  Scope of investigation

The Supervising Scientist’s investigation into the Ranger leach tank failure of 7 December 2013 is confined to the assessment of the potential impacts on human health and the offsite environment, including Kakadu National Park, as a result of the incident. The Supervising Scientist’s investigation does not consider the cause of the leach tank failure, nor does it consider issues related to the condition of the Ranger processing facility, as this remains the subject of ongoing investigations by the Northern Territory Department of Mines and Energy and Northern Territory WorkSafe.

## 1.2  Ranger uranium mine

The Ranger uranium mine (Ranger) is located in the Alligator Rivers Region, approximately 250 km east of Darwin and 6 km east of the township of Jabiru. Ranger is situated adjacent to Magela Creek; upstream of the Ramsar listed Magela wetlands and surrounded by the World Heritage listed Kakadu National Park (Figure 1.1).

Ranger is currently the only operational uranium mine in the region, and is owned and operated by Energy Resources of Australia Ltd (ERA). Production commenced at Ranger in August 1981, with milling expected to continue until 2021. Ranger is a conventional open pit mining operation utilising an acid leach process. Mining in Pit 3 ceased in November 2012; with the operation now solely processing stockpiled ore.

The climate of the Alligator Rivers Region is dominated by a seasonal wet-dry monsoon cycle. The wet season generally extends from late October to early April with predominantly north westerly winds, while the dry season is dominated by easterly to south-easterly winds and extends from May to September. The average annual rainfall is approximately 1 600 mm with around 1 300 mm falling between December and March.

Ranger is located on gently undulating lowlands adjacent to the sandstone escarpment of the Arnhem Plateau. The primary land-cover is open savannah woodland with narrow zones of dense riparian vegetation restricted to watercourses and wetland fringes.

### 1.2.1  Overview of Ranger water classes

There are several water classes used at Ranger based on water quality. Classes include Process water, Pond water and Release water as shown in Figure 1.2.

Figure 1.1  The Alligator Rivers Region.

Figure 1.2  Water class catchments on the Ranger mine site (ERA 2013).

Each class of water differs according to its physico-chemical composition (Table 1.1), which dictates the way it is managed. The process water inventory is derived from waters that have come into contact with the uranium extraction circuit and from rainfall on the designated process water catchments, including the Tailings Storage Facility (TSF). Process water is characterised by a very high dissolved salt load.

The pond water inventory is derived from rainfall that falls on the active mine-site catchments, generating water of a quality that requires active management. Pond water typically includes:

Seepage and surface water runoff from the mineralised rock stockpiles;

Seepage from the low-grade rock stockpiles, and

Runoff/discharges from the processing areas not directed to the process water circuit.

The main storage facilities for pond water are Retention Pond 2 (RP2), Retention Pond 6 (RP6) and Ranger Pit 3. Pond water is able to be reused on the Ranger project area for a variety of uses including dust suppression onsite including within the secondary crushing dust management process; ore processing; vehicle washing; fire control and cooling water in the power station. While of significantly better quality than process water, pond water is characterised by an elevated dissolved salt load.

Table 1.1  Indicative Water Quality of Water Classes (from ERA 2013).

| Parameters | Process Water | Pond/ Water (RP2) | Managed Release Water (RP1) | Potable Water | Water Treatment Plant Permeate |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Process Water Permeate | Pond Water Permeate |
| pH | 3.8 | 8.2 | 7.3 | 7.9 | 7.0-8.0 | 7.0-8.0 |
| EC (μS cm-1) | 23,545 | 1,490 | 615 | 390 | < 200 | < 200 |
| Phosphorus (mg L-1) |  |  |  |  | < 0.01 |  |
| Aluminium (mg L-1) | 330 | 0.1 | 0.005 | 0.001 |  |  |
| Calcium (mg L-1) | 475 | 40 | 10 | 30 |  |  |
| Magnesium (mg L-1) | 4,735 | 205 | 75 | 45 |  |  |
| Manganese (mg L-1) | 1,930 | 0.1 | 0.01 | 0.001 |  |  |
| Uranium (mg L-1) | 25 | 5 | 0.01 | 0.01 | < 0.04 | < 0.04 |
| NH3 (mg L-1) | 780 | 0.05 | 0.05 |  | < 2 |  |
| Sulphate (mg L-1) | 27,985 | 855 | 280 | 2 |  |  |
| 226Ra (mBq L-1) | 9,680 | 2,300 | 115 |  | < 100 | < 100 |

Retention Pond 1 (RP1) is a managed release system. During periods of managed release in the wet season, water discharged over the RP1 weir is directed into Coonjimba Billabong and, ultimately, into Magela Creek. RP1 water can also be pumped via a pipeline to Magela Creek at MG001. The main influences on the composition of RP1 water include land application areas in the RP1 catchment, pond water treatment plant permeate and rainfall. Runoff from the trial landform (TLF) and northern TSF 1 stockpile reports to RP1SED (Retention Pond 1 Sedimentation Bund) which then passively flows to RP1.

## 1.3  Legislative framework

Ownership of uranium in the Northern Territory remains vested in the Commonwealth in accordance with S35 of the Atomic Energy Act 1953 and S69(4) of the Northern Territory (Self Government Act) 1978. This is given effect in Northern Territory legislation by S34 of the Mining Management Act 2013 and S175 of the Mining Act 2007 which require the Territory Minister to act in accordance with the advice of the Commonwealth Minister in regard to uranium mining.

Responsibility for the regulation of uranium mining has been delegated to the Northern Territory via a series of inter-governmental agreements, the 2000 agreement Principles to be applied in the regulation of uranium mining in the Northern Territory and the subsequent 2005 Memorandum of understanding between the Commonwealth of Australia and the Northern Territory of Australia in relation to working arrangements for the regulation of uranium mining in the Northern Territory which outline the respective roles and functions of the Territory and Commonwealth agencies (including the Supervising Scientist) involved in uranium mining regulation in the Northern Territory.

The position of the Supervising Scientist is established under the Environment Protection (Alligator Rivers Region) Act 1978 for the purpose of ensuring the environmental protection of the Alligator Rivers Region from the potential impacts of uranium mining, including oversight of the regulation of uranium mining.

Ranger operates under Authorisation 0108–16 granted by the Northern Territory Minister under the Mining Management Act 2013, and in accordance with the Environmental Requirements of the Commonwealth of Australia for the Operation of the Ranger Uranium Mine (the Environmental Requirements) attached to both the Atomic Energy Act 1953 Authority, which establishes the Ranger Project Area, and ERA’s uranium export permit granted under the Customs (Prohibited Exports) Regulations 1958.

The Environmental Requirements for Ranger have been incorporated into the Mining Management Act 2013 Authorisation and stipulate amongst other matters, considerations for the protection of the environment, rehabilitation of the site and expectations in relation to statutory planning, reporting and inspection regimes.

## 1.4  The Supervising Scientist monitoring program

The Supervising Scientist conducts a program of chemical, biological and radiological monitoring in the region to ensure the environment remains protected from the potential impacts of uranium mining. Figure 1.3 shows key monitoring sites including continuous water quality monitoring locations in Magela and Gulungul creeks, which record conductivity, turbidity and pH and are equipped to take automatic samples and send alarm notifications if pre-determined water quality triggers are exceeded (Supervising Scientist 2012). This real-time monitoring capability is supplemented by a program of biological monitoring, including in situ toxicity testing, and an air monitoring program to detect any changes in airborne radioactivity concentrations.

Findings from, and full details of, the monitoring program are published annually in the Supervising Scientist annual report (available at www.environment.gov.au/SSD), with water chemistry information published weekly on the Supervising Scientist Division (SSD) webpage during the wet season and reported biannually to the Alligator Rivers Region Advisory Committee.

Figure 1.3  Ranger minesite.

# 2  Description of the incident

## 2.1  Incident summary

At approximately 00.10 am on Saturday 7 December 2013 operators in the processing area at Ranger observed slurry under pressure being released from the wall of Leach Tank 1 through a hole approximately 2 m above the base of the tank. ERA staff attempted to contain the leaking material in the concrete bunded area of the leach tanks. All personnel were evacuated from the area at approximately 00.40 am following the identification of a second leak. At 00.54 am Leach Tank 1 catastrophically failed, releasing approximately 1 400 m3 of slurry into the surrounding processing area (Figure 2.1).

The Supervising Scientist was advised of the incident at 06.20 am on 7 December and commenced assessment and monitoring of potential impacts from the incident as discussed in Section 3.

Figure 2.1  Collapsed Leach Tank 1.

## 2.2  Ranger mine Leach Tank Incident Task Force

Following the leach tank failure at Ranger a task force, consisting of representatives from SSD (the Australian Government Department of the Environment), the Australian Government Department of Industry (DoI), the Northern Territory Government Department of Mines and Energy (DME), Northern Territory WorkSafe, the Northern Land Council (NLC) and Gundjeihmi Aboriginal Corporation (GAC), was established to coordinate the separate incident investigations of the various agencies. ERA had voluntarily stopped production immediately following the incident. On 9 December 2013 the CEO of the Northern Territory Department of Mines and Energy and the Commonwealth Minister for Industry then directed ERA that ore processing operations at Ranger should remain ceased until such time as they deemed it safe for operations to recommence.

Following a tender process commencing in January 2014, the Australian Government Department of Industry engaged independent experts Noetic Risk Solutions and HRL Technology in late February 2014 to conduct a risk-based assessment of the Ranger processing facility, including examination of ERA’s maintenance practices and operational governance arrangements.

Subsequently the independent experts provided a report to the Task Force recommending that processing operations may be recommenced subject to certain conditions. This report was then subject to independent peer review prior to the Commonwealth Minister for Industry and the CEO of the Northern Territory Department of Mines and Energy providing permission for ERA to recommence processing operations on 4 and 5 June 2014 respectively.

Commensurate with the role of the Supervising Scientist, SSD has undertaken a separate investigation into the potential impacts on human health and the offsite environment, including Kakadu National Park, as a result of the incident.

## 2.3  Leach slurry properties

Tables 2.1 and 2.2 present the physical and chemical details of the tank and slurry relevant to the investigation. The leach tanks form the first phase of ore processing with no concentration of uranium occurring at this point in the process. Hence the radiological properties are essentially equivalent to stockpile material. The leach slurry is a mix of ground ore, sulfuric acid and water, undergoing leaching to extract the uranium from the solid ore into the aqueous phase for subsequent refinement in further processing stages.

Table 2.1  Slurry material and leach tank details

| Tank Capacity | 1 450 m3 |
| --- | --- |
| Volume of slurry | 1 400 m3 |
| Percentage Solids | 36.9% |
| Density of Slurry | 1.35 t m-3 |
| Leach tank bund capacity | 1 666 m3 |
| Uranium Ore Grade | 0.16% |
| Ore/Slurry Temperature | 55 °C |

Table 2.2  Slurry chemical properties

| pH | 1.21–1.89 |
| --- | --- |
| Sulfate (mg L-1) | 29 800 |
| Magnesium (mg L-1) | 4 510 |
| Magnesium:Sulfate (ratio) | 3 : 20 |
| Calcium (mg L-1) | 387 |
| Manganese (mg L-1) | 1 340 |
| Uranium (mg L-1) | 386 |

Note: These values represent the maximum concentrations based on samples 
taken at the grinding circuit and towers on 6 December 2013

## 2.4  Spatial extent of the spill

Leach Tank 1 failed towards the north-west with the slurry being expelled in that general direction. The slurry was primarily dispersed between the leach tanks and RP2 and remained within the processing area and adjacent service roads (Figure 2.3). It was identified that an unknown quantity of the slurry entered the storm water drainage system and thereby reported to RP2. No rainfall events occurred between the time of incident and the isolation of the storm water drains, hence no further material entered the drainage system. The extent of the spill in the context of the surrounding environment is shown in Figure 2.2.

The area impacted by the spill comprised four main groundcover types, namely concrete bunded areas, earthen hardstand, grass and bitumen/concrete (including roadways). A breakdown of the area impacted for each surface type is shown in Table 2.3. The extent of the spill, broken down by groundcover type, is shown in Figure 2.3.

Table 2.3  Estimated spill area by groundcover type (ERA data).

| Surface type | Area m2 | % of total |
| --- | --- | --- |
| Bitumen/concrete | 3 570 | 24.2 |
| Bund (Concrete) | 4 220 | 28.6 |
| Grass | 30 | 0.18 |
| Earthen Hardstand | 6 930 | 47.0 |
| Total | 14 750 | 100 |

Figure 2.2  Ranger minesite showing spatial extent of the slurry spill.

Figure 2.3  Slurry spill area by groundcover type. ERA data.

An assessment of the level of slurry in the leach tank bund immediately after the incident suggests that the bund was approximately half filled (Figure 2.4). The leach tank bund capacity is 1 666 m3 (ERA data). It is estimated approximately 700–800 m3 of slurry was retained in the bund with the remaining 600–700 m3 spilling outside the bund. Whilst there was sufficient capacity to contain the entire volume of the leach tank within the bund, by its nature bunding is designed to contain minor spills and leaks and not catastrophic failure.

Figure 2.4  Leach tank bund following the failure of Leach Tank 1.

## 2.5  Cleanup operation

Following the failure of Leach Tank 1, drains in the plant area were closed with sandbags and earthen bunds to prevent any further transport of slurry to RP2. This work was completed prior to Supervising Scientist staff arriving on site on the morning of 7 December 2013.

Blue metal/cracker dust was then spread over the slurry to absorb any liquid and then scraped up by bobcat (Figure 2.5) for removal and final disposal in Pit 1.

Once scraped the areas were then washed down with water collected and removed via vacuum truck for disposal to the tailings dam.

With the exception of the exclusion zone established around the failed tank, the major cleanup activities were completed within four days and were inspected by SSD, DME, NLC and GAC during the Routine Periodic Inspection on 12 December 2013.

Figure 2.5  Scraped grass verge following cleanup. Grass cover adjacent to the road verge was removed during clean up.

# 3  Supervising Scientist Division Response

Potential pathways for environmental impacts were evaluated in conjunction with the initial response detailed in Section 3.1. The critical pathways were broadly grouped into the following categories:

surface water

groundwater, and

radiological

## 3.1  Initial response

### 3.1.1  SSD initial site inspection

Saturday 7 December 2013

Representatives from SSD Jabiru Field Station (JFS), Northern Land Council (NLC) and Gundjeihmi Aboriginal Corporation (GAC) inspected various areas of the site around the failed leach tank. It was observed that slurry from the leach tank had filled low lying areas such as roads and drains and flowed in a north westerly direction for approximately 200 m (Figure 3.1 and Figure 3.2).

| Figure 3.1 Looking south east at the failed tank from the end of the slurry flow. | Figure 3.2 Lateral spread of the slurry in low lying areas. |
| --- | --- |

The extent of the spill was able to be clearly identified due to the colouration of the slurry. The ERA Water Management Team reported no visual evidence of slurry in RP2. ERA advised that they intended to use earthen bunds to control any runoff from rainfall.

ERA spread and mixed blue metal/cracker dust over the slurry on the roads so that it could then be removed to Pit 1 for disposal. The ERA radiological team was required to sample and clear areas following removal of the slurry and blue metal/cracker dust mixture prior to further cleanup operations including the washdown of Zone 1 on 11 December 2013 (Section 3.2.1.2.).

Samples were obtained by SSD from the upstream and downstream Magela Creek water quality monitoring sites and dispatched for radium-226 (226Ra), total metals and filterable metals analysis.

### 3.1.2  Supervising Scientist’s inspection

Sunday 8 December 2013

A site inspection of Ranger was conducted by the Acting Supervising Scientist, the Director Office of the Supervising Scientist and the Program Leader Environmental Radioactivity in response to the leach tank failure of 7 December.

The site of the incident was inspected, including the failed leach tank and surrounding structure. It was noted that the structure was not fully stable and that an exclusion zone had been established surrounding the failed tank to protect the safety of workers in the event of any further collapse. ERA informed the team that a structural engineer was onsite and working to assess the stability of the structure. At the time of the inspection, the remaining leach tanks had not been drained pending advice from the structural engineer.

The inspection team walked the full circumference of the slurry spill to ascertain the aerial extent; gamma dose readings were collected at ten locations. These results are discussed in subsequent sections of this report. The extent of the spill was able to be clearly identified due to the colouration of the slurry, and it was evident that the spill had remained within the plant area with an unknown quantity having reported to the storm water drains and from there to RP2. Slurry residue was visible in the storm water outfall at RP2, although there was no flow at the time of the inspection.

Cleanup works were underway with a substantial amount of slurry having been removed from roadways and hardstand areas. It was noted that workers conducting the cleanup were wearing radiation monitoring equipment and SSD requested the results once available (Section 4.3). The stormwater drain system had been blocked off with sandbags and earthen bunds to prevent further slurry reporting to RP2 in the event of any rainfall. ERA advised the spilt material was being stockpiled on the Run of Mine (ROM) pad (Figure 1.3).

The inspection team were advised that cleanup works were expected to take a further two days to complete, with the area immediately surrounding the failed tank to remain as it was not currently safe to enter. The exclusion area surrounding the failed tank had been surrounded with an earthen bund.

Discussions were held with the ERA General Manger Operations and the Manager Health Safety Environment Water regarding ERA’s plans for cleanup and recovery. It was confirmed that the processing plant had been stopped immediately after the incident and ERA was advised not to recommence processing. ERA was requested to cease pond water treatment until such time as any impacts on RP2 water quality could be determined. ERA was advised to treat the area of the spill as a process water catchment until cleanup operations had been completed.

The SSD offered to provide independent health monitoring (through urinalysis) for any workers concerned about potential exposure to the leach material. However, no requests for urinalysis were received following the incident.

### 3.1.3  Routine Periodic Inspection

Thursday 12 December

The December Routine Periodic Inspection was held on 12 December 2013 and attended by representatives from SSD, DME, NLC and GAC. A briefing on the leach tank incident was held upon arrival at site. Removal of material from the remaining leach tanks was underway with Leach Tank 2, adjacent to the failed tank, being maintained at approximately 2/3 volume to assist with structural stability. This leach tank material was pumped to the TSF. ERA advised that at the time of incident approximately 1 300 m3 of slurry material at 45% solids was contained in Leach Tank 1, which had a total capacity of 1 450 m3. This information was later corrected to 1 400 m3 and 37% solids based on review of operational data.

Specialist deconstruction contractors were to arrive the week commencing 16 December 2013 to assess deconstruction options. Pre-planning of isolation and re-routing of cabling had commenced. A list of potential independent experts to conduct the ERA internal investigation was before the company board for consideration.

ERA confirmed all relevant drains had been covered with plastic and sandbags to prevent any further mobilisation of slurry material to RP2. ERA indicated that some slurry had entered the drainage system reporting to RP2 and may have still been within the drainage system pending flushing. It was confirmed that ERA daily collection of water samples from RP2 would continue and this may be reviewed following significant rain events. ERA confirmed pond water treatment had ceased until water quality impacts on RP2 were assessed. ERA confirmed there would be no disposal of any material evidence that may be required for internal and external investigators.

A walk through was conducted of the immediate area of impact. Primary and secondary containment bunding had been established (Figure 3.3) to broadly separate the slurry impact area into three main zones, Zone 3—the immediate vicinity of tank; Zone 2—adjacent hardstand and impacted crushing circuit, and Zone 1—a wider impacted zone including roads and grass areas (Figure 3.4). All drains inspected were blocked with plastic sheets and sandbags to restrict any further movement of material into the drainage system (Figure 3.5). Surface cleanup had occurred including removal of slurry from main roads and topsoil removal from grassed areas adjacent to these roads.

During the walk through, gamma dose rates were recorded by SSD staff for the areas previously surveyed during the Supervising Scientist’s inspection of 8 December (Section 3.1.2).

Figure 3.3  Containment bunding between RP2 and leach tanks.

Figure 3.4  Classification of impact zones for wash down purposes.

Figure 3.5  Example of drain blockage.

## 3.2  Surface Water

### 3.2.1  Onsite surface water

#### 3.2.1.1  Retention Pond 2 (RP2)

RP2 is the primary pond water storage which came into contact with the slurry from the incident and, therefore, was the primary location for monitoring of onsite surface water impacts.

RP2 comprises an earthen embankment forming an impoundment providing approximately 1 090 ML of storage. The RP2 catchment area covers 161 ha including the active mine-site area, most mineralised rock stockpiles, stormwater runoff from the plant footprint and pond water outflows from the processing plant (Figure 1.2). Pond water inventory is primarily derived from rainfall that falls on the active mine-site catchments, generating water of a quality that requires active management and treatment prior to release. The inventory of pond water within RP2 is reduced via evaporation and treatment through three microfiltration-reverse osmosis water treatment plants prior to discharge.

Following the initial collection of samples by SSD from RP2 associated with the wash down inspection of Zone 1 on 11 December 2013 (Section 3.2.1.2), further water samples were collected from RP2 on 18 and 23 December 2013 and 7 January 2014 by representatives of SSD accompanied by ERA staff. These were analysed for filtered and total metals and 226Ra as per the methodology outlined in Supervising Scientist (2012).

Water quality monitoring data collected by SSD and ERA both historically and around the period of the incident have been collated and analysed and are discussed below. For the purposes of this report, the discussion of physico-chemical parameters will be limited to electrical conductivity (EC), pH and indicators of process water as identified in Weaver et al. (2010), namely calcium (Ca), magnesium (Mg), manganese (Mn) and sulfate (SO4). Uranium (U) concentration and 226Ra activity concentration are also included. Filterable (< 0.45 µm), residual (> 0.45 µm) and total (filterable + residual) sample results are discussed.

#### 3.2.1.2  Process to Pond water catchment clearance

Areas impacted by the slurry included regions that were part of the pond water catchment including service roads and hardstand areas outside of the primary containment bunding of the leach tanks. As these areas essentially contained process water from the slurry, they were reclassified as part of the process water circuit, with all surface water (including rainfall) captured in these areas to be treated as process water. This required isolation of these areas from the surrounding pond water catchments through the blocking of stormwater drains and the establishment of earthen bunding around the perimeter to ensure surface water was contained.

As part of the cleanup operations, the impact area from the slurry was broadly separated into three main zones as identified during the routine periodic inspection (Section 3.1.3). These three zones are shown below in Figure 3.5. The purpose of this zoned approach was to facilitate a return to the pond water system of those areas impacted by the slurry once a specific area had been sufficiently cleaned.

An assessment of runoff water quality was used to verify the area was suitable to be reincorporated into the pond water system. This was done during the final cleaning of each of the three zones (Section 4.1.2.2). The method of cleaning the three zones was different between Zone 1 and Zones 2 and 3. Zone 1 involved utilising a water cart carrying pond water quality RP2 water to spray onto roads and road verges and was conducted on the 11 December 2013. Zones 2 and 3 were assessed on the 19 December 2013 and 19 March 2014, respectively. In these zones rainwater which had recently fallen onto the scraped hardstand/bitumen and pooled was sampled. This second method is analogous to the generation of much of the pond water quality run-off from the mill, i.e. clean rain falling on the processing plant footprint. The Zone 1 method generates run-off which will inherently be of increased concentration compared to RP2 water as the run-off is generated by pond water and not clean rain water.

##### Surface soil sampling

Wednesday 11 December 2013

Representatives from SSD conducted surface soil sampling at Ranger associated with the cleanup of Zone 1 on Wednesday 11 December 2013.

Composite soil scrape samples were collected from the road verges in front of the acid plant and under the crushing transfer tower (Figure 3.6). At each of these locations, samples were collected in areas that had been exposed to the slurry (SS1 and SS3), and corresponding control samples were collected in areas where it was indicated by ERA that the slurry had not reached (SS2 and SS4). The samples were collected at each site using a plastic trowel to scrape approximately the top five centimetres of soil from three randomly selected locations (composited) within a 0.5 m2 area. General methods for soil sampling are outlined in Saynor et al. (2001).

The soils were assessed for their potential to release slurry-related elements into rainwater runoff by performing a 1:20 water leach (AS4439.2) followed by ICP-MS and OES analysis on the leachate. The results are reported in section 4.1.2.2.

Figure 3.6  Sample locations for soil scrapes.

##### Clearance of Zone 1

Wednesday 11 December 2013

Representatives of SSD conducted water sampling at Ranger during the cleanup of Zone 1 on Wednesday 11 December 2013.

A water cart of approximately 8 000 L was utilised to spray RP2 water onto road verges and the road in areas that had been exposed to the spilled slurry. Water samples were then taken where the resulting water ponded in the stormwater drains as shown in Figure 3.7.

Figure 3.7  Sample locations for Zone 1 clearance.

The water cart was also utilised to flush water down through the stormwater system with samples collected in RP2 at the outflow of the central and western drains.

At each sampling site, SSD collected water samples for analysis of filtered and total metals, general water quality parameters (including EC and pH) and total 226Ra as per the methodology outlined in Supervising Scientist (2012). Results of this water sampling are detailed in Section 4.1.2.2.

##### Clearance of Zone 2

Thursday 19 December 2013

Representatives from SSD conducted sampling associated with the cleanup of Zone 2 accompanied by staff from ERA on Thursday 19 December 2013.

Rainfall records for the Jabiru Airport indicate 36.6 mm of rain fell on 15 December 2013, 9.8 mm on 16 December 2013 and 11.2 mm on 19 December 2013. There was adequate pooling of rainwater remaining from these events to obtain the required samples. Additional RP2 water was not required to wash the area down.

Six pools of water were sampled within Zone 2 (Figure 3.8). At each sampling site SSD, collected water samples for analysis of filtered and total metals and 226Ra. Results of this water sampling are detailed in Section 4.1.2.2.

Figure 3.8  Sample locations for Zone 2 clearance.

##### Clearance of Zone 3

Wednesday 19 March 2014

Representatives from SSD conducted sampling associated with the cleanup of Zone 3 accompanied by staff from ERA on Wednesday 19 March 2014.

Rainfall records at the Jabiru Airport indicate 35 mm of rain fell on 15 March, 9.6 mm on the 16 March and 1.6 mm on the 17 March 2014. There was adequate pooling of rainwater remaining from these events to obtain the required samples. Additional water was not utilised to wash the area down.

Two locations within Zone 3 had been excavated, associated with repair of the concrete bund wall around the failed tank (Figures 3.9–3.10). Both of these areas would drain into the tank bund area and thereby report to the process water circuit.

| Figure 3.9 Excavated area within Zone 3 | Figure 3.10 Excavated area within Zone 3 |
| --- | --- |

One pool of water was sampled within Zone 3 (Figure 3.11). SSD collected water samples for analysis of filterable and total metals and filterable 226Ra. Results of this water sampling are detailed in Section 4.1.2.2.

Figure 3.11  Sample location for Zone 3 clearance.

### 3.2.2  Offsite surface water

#### 3.2.2.1  Magela Creek sampling

Continuous monitoring of water quality parameters (EC, turbidity and pH) commenced on 28 November 2013 at the SSD monitoring sites, upstream (MCUGT) and downstream (MCDW) of Ranger (Figure 3.12) as part of SSD’s routine wet season monitoring program.

SSD staff collected water samples at the MCUGT and downstream MCDW monitoring sites on 7, 9–13, 17, 19 and 23 December 2013. These samples were analysed for filterable and total metals, and total 226Ra as per the methodology outlined in Supervising Scientist (2012).

The automatic sampling equipment at the MCUGT and MCDW sites was utilised to collect water samples on 26 and 30 December 2013 and 2 January 2014 (samples were retrieved by SSD staff on 2 January 2014). These samples were analysed for total metals as per the SSD routine methodology (Supervising Scientist 2012) and results are presented in Section 4.1.2.

Figure 3.12  Location of Magela Creek Upstream (MCUGT) and Magela Creek Downstream (MCDW) monitoring sites.

#### 3.2.2.2  In situ toxicology testing

5–9 December 2013

SSD conducts a fortnightly routine in situ toxicity testing program in Magela Creek which measures the reproduction (egg production) by the freshwater snail, Amerianna cumingi. Each test runs over a four day (96 hr) exposure period with the snails placed in floating (flow-through) containers located in the creek.  Standardised laboratory toxicity test protocols have shown that of SSD’s suite of six local species, this species is among the most sensitive to continuous exposures of U (Hogan et al. 2010), Mg (van Dam et al. 2010) and Mn (Harford et al. 2014).

The acid leach tank failure on 7 December 2013 coincided with an in situ toxicity test being conducted in Magela Creek (deployed on 5 December 2013 and retrieved on 9 December 2013). Subsequent tests were conducted on a fortnightly basis in Magela Creek, being deployed on a Thursday and retrieved the following Monday with results presented in Section 4.1.3.2.

After each wet season, toxicity monitoring results for the tests are analysed, with differences in egg numbers (the ‘response’ variable) between the upstream (control) and downstream (exposed) sites tested for statistical change between the wet season just completed and previous wet seasons. This Before-After Control-Impact Paired (BACIP) design, with ANalysis of VAriance (ANOVA) testing, is described further in the Supervising Scientist Annual Report for 2007–08 (Section 2.2.3).

## 3.3  Groundwater

### 3.3.1  Soil profiling

In order to determine the potential for offsite effects from the leach tank spill via the groundwater pathway, it is necessary to characterise the properties of the surficial material onto which the leachate spilled. This is to understand whether the material is able to act as a conduit, enabling the infiltration of leachate into the subsurface and also if there are any chemical or mineralogical processes which may bind or disperse any contaminant.

Properties of soils at the Ranger site have been investigated in previous studies. Chartres et al. (1991) provides a general description of Ranger mine soil types, and Hollingsworth (2006) and Alarcon Leon et al. (2007a) investigate the soils at the mine for potential contamination.  While these provided some necessary background information, they were not deemed suitable or sufficient to fully interpret the surficial material properties at the site of the spill. Existing soil survey information (Wells 1979, White & McLeod 1985) was considered too small and lacked detail for the present purposes.

In order to provide sufficient detail, the soils and surficial materials at five holes in the Ranger mill area were sampled to a depth of 1 m. The five hole locations in relation to the leach tank spill are shown in Figure 3.13. They included 2 sites (holes 1 and 3) that were affected by the spill and 3 sites (holes 2, 4 and 5) that were unaffected by the spill were assessed as control sites.

The holes were dug by ERA and sampled by SSD during March and April in 2014. The pits exposed the stratigraphy of the site and, where possible, each visible layer was sampled.

Hole 2 was dug by a power auger mounted on a bobcat. The remaining holes were excavated with a backhoe. Hole 2 was completely mixed by the auger and so samples were collected at each 0.2 m layer to a depth of 1 m.

At each site, surficial material was classified according to the methods of McDonald & Isbell (2009) as outlined in the 3rd Edition of The National Committee on Soil and Terrain’s Australian Soil and Land Survey Field Handbook.

Figure 3.13  Location of soil profiles

Soil profiles for each of the five holes were described. In these descriptions, their compositions, including the percentage abundance of different grains such as sand, clay or gravel, were included. Approximate grain size distributions were estimated.  This information is essential to classify the material. It is especially useful to determine the porosity and permeability of the material in order to estimate the likelihood of infiltration. The results of this soil profiling work are presented in Section 4.2.1.1.

The potential for contaminant transport vertically through the 1 m soil profile was investigated. Sub-samples from each of the profile layers were analysed for bound chemical constituents using a sequential extraction process. A low recovery extraction was carried out to simulate the effect of rainfall (1:20 water leach, AS4439.2) and a higher recovery acid extraction (mixed nitric acid/perchloric acid) was carried out to examine the reactivity of the soils and also to determine the extent of possible slurry infiltration. The water leach was carried out on dried, whole samples and the acid extraction was carried out on dried and ground (< 2 mm) samples. The results are presented in Section 4.2.1.2.

### 3.3.2  Groundwater impact assessment by Geoscience Australia

Geoscience Australia (GA) was commissioned to provide advice on the potential for spill-related contaminants to enter the offsite environment via the groundwater pathway. GA has based this assessment on a review of data from groundwater monitoring, hydrogeochemistry, groundwater and hydrogeochemical modelling and geological data provided by SSD and ERA.

An extensive literature and data review was conducted to understand the hydrogeological context of the Ranger minesite (Appendix A). In order to conduct detailed analyses of groundwater levels and flow, GA requested groundwater level data from bores identified to be within 1 km of the spill extent. These groundwater level records covered a date range of January 1981 to January 2014. They analysed long-term seasonal average groundwater levels for the wet and dry seasons and annual seasonal average groundwater levels. Sufficient data to provide an annual seasonal average groundwater level assessment were only available for the 12 month period of the wet season of 2008–09 and the dry season in 2008. Evaluating averaged datasets has limitations, but also has the benefit of identifying longer-term trends in the groundwater levels, and subsequent flow paths and gradients beneath and around the plant site. Surface water flow data in Corridor Creek was also evaluated with respect to rainfall, in order to investigate any potential relationship between surface water and groundwater.

GA undertook an analysis of hydrogeochemistry data of bores in the plant area, in order to understand pre-spill hydrogeochemical conditions of the aquifers and, if possible, determine whether any changes had occurred post spill. Understanding of hydrogeochemistry enables predictions to be made about soil-water and contaminant transport reactions that may occur, should any leachate have entered the aquifer system as a result of the spill. The data for these analyses were provided by ERA. GA requested all hydrogeochemical analyses from bores within a 1 km radius of the spill extent. Samples were taken between March 1982 and January 2014. Sulfate has been identified as the most conservative ion associated with leached ore (Klessa 2001). In addition, Alarcon Leon et al. (2007a) identified sulfate as a key tracer of pre-spill contamination from the plant area. In the current assessment, sulfate was used as an indicator to map the pre-spill contamination extent in groundwater under the plant area. Sulfate in groundwater was interpolated from averaged data collected between 2006 and 2013. Averaged bicarbonate and pH data for the same period were processed in the same manner. Insufficient data were available to enable post-spill hydrogeochemical mapping to be undertaken. Consequently, individual bores were assessed to characterise the hydrogeochemistry of groundwater in the vicinity of Leach Tank 1 prior to the spill.

Only two post-spill hydrogeochemical samples were taken by ERA in the Corridor Creek catchment immediately following the spill, at bores 35 and 36 (as shown in Figure 23 in Appendix A). They are in the plant area but from existing contaminant maps are probably outside the pre-spill plume extents. These bores were sampled by ERA six days after the 7 December 2013 Leach Tank 1 spill. Following recommendations by GA, on 14 February 2014, SSD requested ERA commence a groundwater monitoring program in the spill area. ERA obtained the first samples related to this request on 2 April 2014. Samples were then collected weekly for 5 weeks prior to reducing to monthly. Sample data was provided to SSD and GA for analysis. The 6 week timeframe for the commencement of monitoring reduces the ability of the program to definitively determine pre-spill groundwater characteristics as, while it is unlikely, it is possible that by April 2014 contamination from the spill could have already impacted on the bores in question. As such, while it is likely that data from these bores do represent background groundwater conditions for the plant area, this cannot be stated with absolute certainty. This delay and resultant introduction of uncertainty into the assessment of background conditions highlighted the importance of timeliness in ERA’s response to requests for investigative actions.

By collating and interpreting all derived information, a hydrogeochemical impact analysis was also conducted, based on an estimation of how much leachate may have infiltrated post-spill. Results are summarised in Section 4.2.2. Full details of the methodology and results can be found in Appendix A.

## 3.4  Radiation exposure

### 3.4.1  Gamma dose rate measurements on site

Sunday 8 December 2013

During the Supervising Scientist’s inspection (Section 3.1.2) measurements of external gamma dose rate were taken along the perimeter and within Zone 1 of the spill area.

An Automess dose rate meter (model: 6150 AD 5/H), which provides gamma dose rate readings in digital and analogue form simultaneously, was connected to a gamma probe (Geiger Müller tube, model: 6150 AD-18/H). The 6150 AD-18/H GM tube has a gamma dose rate measurement range of 0.1 µSv hr-1 to 10 mSv hr-1 (Automess 2013). The dose rate meter and GM tube were calibrated by the Queensland University of Technology Radiological Laboratory, 19 January 2014. The calibration confirmed that the instrument was working within its specifications.

Measurements were taken approximately 1 m above the ground surface, allowing the GM tube to adjust to the gamma radiation field at the measurement locations for about 30 seconds before a reading was taken. Figure 3.14 shows the extent of Zone 1, the measurement locations and magnitude of the measured gamma dose rates.

Figure 3.14  Results of the gamma dose rate measurements taken around the perimeter of the spill impacted area and within Zone 1 on 8 December 2013.

Thursday 12 December 2013

During the Routine Periodic Inspection, one day after the wash down of Zone 1 (Section 3.1.3), nine measurements of the external gamma dose rate were taken adjacent to areas where gamma dose rates were initially measured on 8 December 2013. Figure 3.15 shows the measurement locations and magnitude of the measured gamma dose rates.

Figure 3.15  Results of the gamma dose rate measurements taken around the perimeter of the spill impacted area and within Zone 1 on 12 December 2013.

### 3.4.2  Radionuclide analyses in the spilled slurry

Samples of the slurry have been collected by ERA after the spill and were sent to SSD for radioanalysis. Table 2.4 shows the sample details. Figure 3.16 shows the locations from which the slurry samples were collected.

Table 2.4  Slurry samples received for analysis

| Sample ID | ERA ID | Received/ collected | Sampling location |  | Mass (g) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | lat, long | easting, northing | mwet | mdry |
| RM13080 | Transfer tower outside bund | 13/12/2013 7/12/2013 | -12.6831, 132.9226 | 274398, 8597015 | 69.15 | 30.14 |
| RM13081 | Transfer tower inside bund | 13/12/2013 7/12/2013 | -12.6833, 132.9225 | 274385, 8596992 | 84.16 | 35.33 |
| RM13082 | Grinding building corner | 13/12/2013 7/12/2013 | -12.6834, 132.923 | 274473, 8596977 | 65.99 | 27.69 |

Figure 3.16  Location of the samples collected by ERA in the morning of 7 December 2013.

Samples of the spilled material were received as wet slurry in the SSD radioanalytical laboratory on 13 December 2013. Immediately after the samples had been received, processing of the samples was started.

Processing of the samples involved the following steps:

Registering the samples in the Environmental Radioactivity Universal Database.

Transfer of the slurry samples into glass centrifuge tubes and centrifugation at 4 400 rpm (revolutions per minute).

Decanting the supernatant and filtration through 0.45 µm polyethersulfone (PES) disposable filter membranes followed by acidification of the filtered sample to 0.5% hydrochloric acid (HCl).

Drying the de-wetted slurry at 60°C in Q geometry containers for gamma spectrometry (Pfitzner 2010).

Sealing the dried slurry in the Q geometry containers for gamma spectrometry analysis.

Performing wet chemistry on the supernatant for 226Ra determination via the BaSO4 method (Medley et al. 2005).

Dispatch of supernatant sub-samples to a NATA accredited laboratory for Inductively Coupled Plasma Mass Spectrometric (ICP-MS) determination of key metals. Results are shown in Tables 4.1 and 4.8.

The dried and sealed slurry samples (2 sub-samples from each original vial) were analysed on the SSD high purity germanium (HPGe) detectors (Murray et al. 1987; Pfitzner 2010) on 16 December 2013, to get an initial estimate of the ore grade. It is important to note that immediate measurement, not allowing for appropriate ingrowth times for radon decay products, will underestimate the activity concentration of 226Ra. This is because the activity of 226Ra in a dried and pressed soil sample is conventionally estimated from the activity of radon decay products, after an ingrowth time of three weeks, to allow radon decay products to reach secular equilibrium with their progenitor, 226Ra (Murray et al. 1987). In contrast, the 238U activity will be overestimated, because its measurement is based on a measurement of the 235U activity at 186 keV, which is corrected for the contribution of gamma rays from 226Ra at the same energy (Esparon & Pfitzner 2009, Pfitzner 2010). This will result in an under-correction of the 235U activity concentration in the samples and consequently higher estimated 238U activity concentrations. Final measurements, allowing for sufficient ingrowth time for radon decay products, were conducted 7 February 2014.

In addition, radionuclides will dissolve through the addition of the dilute sulfuric acid, and this dissolved fraction was not accounted for in the initial results of the dried material. The supernatant has been decanted after centrifugation and before the samples were dried and sealed. The decanted solution has been filtered and analysed separately, using alpha spectrometry methods for 226Ra (Medley et al. 2005) and ICP-MS for U.

# 4  Data analysis and discussion

## 4.1  Surface Water

### 4.1.1  Surface water quality assurance/quality control

The SSD implemented a thorough quality assurance/quality control (QA/QC) program to ensure accuracy and reliability of all water quality monitoring results, including both general parameter data and chemical analysis of collected water samples. This program included analysis of blank and duplicate samples, which were carefully evaluated to assess the overall performance of water sampling techniques and analysis methods. Blank samples were used to detect potential sample contamination occurring during field sample collection and laboratory sample processing. Duplicate samples were used to assess the overall precision and repeatability of field sample collection and laboratory analysis methods.

Blank samples were considered to be acceptable if the analyte concentrations were less than 5 times the analytical detection limit. All blanks were acceptable for all analytes except for dissolved copper and zinc in the filtered samples, which are known to be present in the field filtration units. The maximum blank copper concentration was 0.37 µg L-1 (37 times the detection limit) and the maximum blank zinc concentration was 1 µg L-1 (10 times the detection limit). These were negligible compared to the concentrations in the water samples.

Duplicate samples were considered to be acceptable if the relative percent difference between them was less than 20%. All duplicate samples were acceptable for all analytes.

### 4.1.2  Onsite surface water

#### 4.1.2.1  Retention Pond 2 (RP2)

It was determined that an unknown volume of leach slurry entered RP2 as a result of the failure of Leach Tank 1 on 7 December 2013. The following chemical analysis examines the impact of the slurry on the water quality of RP2. It should be noted in considering the results below that at the time of the incident RP2 contained approximately 500 million litres of water, while the total volume of the spill which escaped the bund was estimated at 600 000–700 000 litres, only a portion of which entered RP2.

##### Electrical conductivity

Continuous electrical conductivity (EC) measured by ERA in RP2 during the 2010–14 wet seasons ranged from a minimum value of 1 096 µS cm-1 recorded on 31 March 2013 to a maximum value of 2 867 µS cm-1 recorded on 22 November 2012 (Figure 4.1A). The EC typically increases during the dry season, caused by a period of dry months during which the solutes in the water evapoconcentrate. During the wet season the EC generally decreases in response to dilution from rain water run-off.

The acid leach tank failure is indicated in Figure 4.1A by a red line. The continuous EC after the incident remained within the range previously recorded. The effect of the incident on the EC of RP2 was indiscernible from the evapoconcentration and dilution cycles observed over previous wet seasons.

Figure 4.1B shows ERA’s RP2 continuous EC data during the period 9 November 2013 to 10 April 2014. During this period the EC fluctuated primarily due to dilution, following significant rainfall events and evapoconcentration during periods of low/no rainfall. However, there was no increase in EC detectable from the incident when compared to the initial level measured on the 11 November 2013.

Figure 4.1C compares two box plots of RP2 continuous EC data, one including three wet seasons of measurements prior to the incident (19 January 2011 to 7 December 2013) and the other including the eight months of continuous measurements after the incident (7 December 2013 to 7 August 2014). While the sample sizes for each box plot are different the comparison shows that there is no substantial change in EC during the eight months following the incident, and that the range of EC measured during this period is within the typical range. A diagram explaining box plot structure is provided in Figure 4.2.

| A |  |
| --- | --- |
| B | C |

Figure 4.1  Continuous Electrical Conductivity (EC) data from RP2 for A) 19 January 2011 to 7 August 2014; B) November 2013 to March 2014; and C) box plots comparing EC in RP2 before (n=25190) and after the incident (n=5841). Data from ERA.

Figure 4.2  Explanatory diagram of a box plot

Note that a minimum number of data points are required to compute each set of percentiles. 
At least three points are required to compute the 25th and 75th percentiles, and at least nine points are required for the 10th and 90th percentiles. If it is impossible to compute a given percentile point, the related graph element is not drawn (ERA 2014).

##### pH

The ERA grab sample data collected over the two seasons prior to the incident show that the RP2 data is circa pH 8, with a range of 7.34 to 9.36 (Figure 4.3A). A slight seasonal variation is observed with the lowest pH values measured at the end of the wet season, due in part to the slightly acidic rainfall that occurs naturally in the region (Noller et al. 1990), and also the influx of (i) runoff from the TSF walls and (ii) water transfers from the western stockpile interception trench.

The pH of the acid slurry was low, between 1.2 and 1.9 (Table 2.2), and the data shown in Figure 4.3A indicate that the pH of RP2 remained around 9 in the weeks following the spill, suggesting that the buffering capacity of the RP2 water was high enough at the time of the spill to neutralise the input of acidic slurry or associated runoff that was generated during subsequent rainfall events or the cleanup process.

| A |  |
| --- | --- |
| B | C |

Figure 4.3  pH data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=68) and after the incident (n=36). Data from ERA.

Figure 4.3B shows the variation in RP2 pH in the weeks following the tank collapse. The measurements taken in the weeks immediately after the incident indicated that there was no discernible acidifying effect caused by input of the acidic slurry. Most of the variation is caused by rainfall events occurring from January onwards, which is partly due to the natural acidity of the rain water but may also be attributed to surface runoff from the spill area entering RP2 via the catchment drainage systems. In all cases the pH quickly recovers and returns to levels greater than 8.

Figure 4.3C compares two box plots of RP2 pH data, one including two full seasons of measurements prior to the incident (13 December 2011 to 29 November 2013) and the other including the seven months of measurements after the incident (7 December 2013 to 7 July 2014). While the sample sizes for each box plot are different the comparison shows that the lowest pH recorded (pH 6.99) occurred approximately two months after the incident. However, the majority of the post-incident pH measurements were more alkaline than the historic median and ranges for both box plots are similar.

##### Magnesium

The dissolved Mg data collected by ERA prior to the incident (between December 2011 and November 2013) show a seasonal variation of approximately 150 mg L-1, with peak concentrations occurring in the late dry season due to evapoconcentration, and the lowest concentrations occurring during the wet season due to dilution from rainfall and input of surface water runoff from pond water catchments on site (Figure 4.4A). The Mg concentration of the leach tank slurry was in excess of 3 000 mg L-1 (Table 2.2).

Figure 4.4B shows no discernible change in the dissolved magnesium concentrations in RP2 due to the input of the leach tank slurry or surface runoff generate by rainfall and the cleanup process. The rainfall throughout January resulted in an almost 50% reduction in RP2 dissolved Mg concentration, which decreased from around 250 mg L-1 to 135 mg L-1. This was the lowest dissolved Mg value recorded in RP2 since December 2011.

The low dissolved Mg concentrations measured in RP2 after the incident are also shown in Figure 4.4C, which compares two box plots of RP2 dissolved Mg data, one including two full seasons of measurements prior to the incident (13 December 2011 to 29 November 2013) and the other including the seven months of measurements after the incident (7 December 2013 to 7 July 2014). The data indicate that the majority of the dissolved Mg concentrations during this period are lower than the 25th percentile of the historical range. These data all indicate that input of the leach tank slurry and subsequent surface runoff from spill zones in the RP2 catchment has not had a detectable impact on the dissolved Mg concentration in RP2.

| A |  |
| --- | --- |
| B | C |

Figure 4.4  Filterable Magnesium (Mg) data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing Mg in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA.

##### Calcium

Dissolved Ca concentrations, both before and after the incident, follow very similar trends to magnesium (Figures 4.5A–C). The mean RP2 Mg:Ca ratio was similar before and after the incident, at 3.79 and 3.66 respectively. Given that the mean Mg:Ca ratio of the acid slurry was 10.7, the similarity between the ratio in RP2 before and after the incident gives further evidence to suggest there was no measureable impact on RP2 for dissolved Mg or Ca levels.

| A |  |
| --- | --- |
| B | C |

Figure 4.5  Filterable Calcium (Ca) data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing Ca in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA.

##### Manganese

Dissolved Mn concentrations measured prior to the incident (ERA grab sample data) are highly variable, with concentrations ranging from 0.4 to 945 mg L-1 (Figure 4.6A). While it is not conclusive, the data suggest a seasonal trend of higher concentrations during the wet season and lower concentrations during the dry season. This is associated with similar trends in the redox conditions of RP2 (data not shown), which influences the formation of insoluble Mn oxide particles.

| A |  |
| --- | --- |
| B | C |

Figure 4.6  Filterable Manganese (Mn) data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=61) and after the incident (n=37). Data from SSD and ERA.

The maximum total Mn concentration measured in the slurry was 1 340 mg L-1 
(Table 2.2). The dissolved Mn results shown in Figure 4.6B indicate that there is no discernible change in concentration immediately following the incident, or during the cleanup process for Zones 1 and 2. However, on 14 January 2014 a dissolved Mn concentration of 2 490 µg L-1 was recorded by ERA, which is considerably higher than the historic maximum observed in data since December 2011 (Figure 4.6A). However this high concentration is equivalent to only 0.2% of the maximum slurry concentration. This data outlier is also shown in Figure 4.6C, which compares two box plots of RP2 dissolved Mn data, one including two full seasons of measurements prior to the incident (13 December 2011 to 29 November 2013) and the other including the seven months of measurements after the incident (7 December 2013 to 7 July 2014). While the median values for both sets of data are similar, a greater proportion of post-incident dissolved Mn concentrations fall in the 3rd quartile at levels above the historical median.

ERA reported to stakeholders in the 13th water quality report for the 2013–14 wet season issued on 10 February 2014 that:

Fluctuations in uranium, manganese and ammonia were observed for samples collected on 14 January 2014. At the time of sampling the water level of RP2 was very low due to the ongoing treatment of RP2 pond water by WTP1 and WTP2. It is believed that as the inventory of RP2 decreased due to treatment from the WTPs, the poorer quality water, located in deeper parts of the pond was sampled. With the large amount of rainfall that has occurred since 14 January 2014, concentrations of uranium, manganese and ammonia have restabilised to be consistent with historical levels as well as the inventory of RP2 increasing.

Statutory water quality monitoring records for RP2 show that dissolved Mn concentrations above 2 500 mg L-1 were recorded on 29 occasions between 1983 and 2000, ranging from 2 600 mg L-1 in 1983 to 22 240 mg L-1 in 2000. Given the occurrence of such high dissolved Mn concentrations in the past; the result from 14 January 2014 is not in itself a definitive indicator of impact from the leach tank incident.

##### Sulfate

Dissolved SO4 concentrations, both before and after the incident (Figure 4.7), follow very similar trends to Mg and Ca (Figures 4.4 and 4.5 respectively). The similarity in the behaviour of the major ions is also shown by the mean Mg:SO4 ratio, which was comparable at 0.218 prior to the incident and 0.22 after the incident. The concentration of SO4 is greater in the slurry due to the addition of sulfuric acid in the acid leaching process. Thus the average Mg:SO4 ratio for the slurry was lower, at 0.15 compared to RP2 pond waters (Table 2.2), however, input of slurry or surface runoff from the spill area has had no discernable impact on the Mg:SO4 ratio of RP2 water following the spill.

| A |  |
| --- | --- |
| B | C |

Figure 4.7  Filterable Sulfate (SO4) data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=62) and after the incident (n=26). Data from SSD and ERA.

##### Uranium

The dissolved U concentrations measured by ERA prior to the incident show a seasonal variation of approximately 6 000 µg L-1, with concentrations ranging from around 
2 000 µg L-1 in the wet season to between 7 000 and 8 000 µg L-1 in the dry season (Figure 4.8A). Like the other solutes discussed, this is due to evapoconcentration during the dry season and dilution during the wet season.

| A |  |
| --- | --- |
| B | C |

Figure 4.8  Filterable Uranium (U) data from RP2 for A) 13 December 2011 to 7 July 2014; 
B) 9 November 2013 to 11 April 2014; and C) box plots comparing EC in RP2 before (n=61) and after the incident (n=37). Data from SSD and ERA.

The dissolved U concentration in the slurry was a maximum of 386 000 µg L-1 (Table 2.2). Figure 4.8B shows the dissolved U concentration in RP2 samples collected over the 4 weeks following the incident. These concentration were the lowest recorded in the last two years of monitoring, and as such, show no evidence of increased concentration in relation to input of the leach tank slurry nor the subsequent rainfall and cleanup generated runoff. Since March 2014 the dissolved U concentration is starting to increase again but the level is still well within the historical range.

Figure 4.8C compares two box plots of RP2 dissolved U data, one including two full seasons of measurements prior to the incident (13 December 2011 to 29 November 2013) and the other including the four months of measurements after the incident (7 December 2013 to 7 April 2014). The data show that, since the incident, the dissolved U concentration in RP2 has been lower than historical levels since December 2011; all the post-incident concentrations are below the historical median of 3 900 µg L-1, and the post-incident 75th percentile concentration of 2 228 µg L-1 was less than the historical 25th percentile concentration of 3 050 µg L-1.

##### Radium-226

Figure 4.9A shows filterable and residual 226Ra activity concentration data for RP2 collected by both ERA and the SSD. Prior to 2002, ERA’s routine water quality monitoring program included analysis of filterable and residual 226Ra activity concentrations in RP2. Since 2002 ERA have only analysed for total 226Ra activity concentrations and routine analysis of 226Ra within RP2 ceased in 2008. For this reason there are only five datapoints within Figure 4.9B. In 2006 Akber et al. (2011) carried out filterable and residual analysis on a single RP2 sample, which is also shown in Figure 4.9A.

Historically, the filterable activity concentrations were less than 5 Bq L-1 and residual activity concentrations were less than 1 Bq L-1 (Figure 4.9A). The SSD samples taken in December 2014 show a filterable activity concentration of 1.14 Bq L-1 and a residual activity concentration of 0.16 Bq L-1. Both of these activity concentrations fall well within the historical range, with the filterable activity concentration being slightly less than the historical median of 1.4 Bq L-1 and the residual activity concentration being similar to the historical 75th percentile of 0.17 Bq L-1.

Total 226Ra activity concentration data measured by ERA and SSD before and after the incident are shown in Figure 4.9B. Three samples collected by ERA between January and April 2012 had total activity concentrations between 2.0 and 2.4 Bq L-1, which are higher than the total activity concentrations measured by SSD and ERA following the incident and the Zone 1 and 2 cleanups. All total activity concentrations measured since December 2013 were less than 1.3 Bq L-1.

Figure 4.9C uses box plots to compare the relative proportion of filterable and residual 226Ra activity (as a percentage of the combined total) in samples before and after the incident. The box plots show that the distribution of 226Ra activity between the filterable and the residual fractions following the incident is similar to the distribution prior to the incident, with around 90% of the 226Ra activity associated with the filterable fraction (< 0.45 µm) and 10% associated with the residual fraction (> 0.45 µm). This, along with the fact that the total activity concentrations measured after the incident are lower than those measured in 2012, indicate that there was no impact on the 226Ra activity concentrations in RP2.

| A |  |
| --- | --- |
| B | C |

Figure 4.9  Radium-226 (226Ra) data from RP2 for A) filterable and residual activity concentrations for 1988–2014; B) total activity concentrations for December 2011 to December 2013; and C) box plots comparing EC in RP2 before and after the incident. Data from SSD and ERA (Akber et al. 2011).

#### 4.1.2.2  Process to Pond water catchment clearance

##### Surface soil scrapes

The water soluble concentrations of elements in exposed soils in the Ranger plant area were compared to the control soils. This was to determine if there were increased amounts of labile soil bound or precipitated elements, from being in contact with the slurry, that could readily be mobilised during rainfall events and eventually runoff into the RP2 catchment area.

In general, the soil concentrations of many elements were higher under the crushing transfer tower compared to the acid plant, for both the control and the exposed soils. This is expected given the years of accumulation of dust and fine particles that fall from the crushed ore that is transferred via the conveyor belt overhead. However, most elements in the crushing transfer tower soils were higher in the control compared to the slurry-exposed soil. This is likely to be because during the cleanup operation, prior to sample collection, the surface layer of the road verge in front of the crushing transfer tower was scraped (using light machinery). While the majority of the soil that was in contact with the slurry was removed, the underlying surface still showed elevated levels of a number of elements.

The key elements that were elevated in the exposed soils (not including the top < 10 cm which had been removed during the clean up immediately after the incident) compared to the control soils at both locations were U, Ca, Mg, Na and S (including SO4 and any other S compounds present). Table 4.1 shows the water soluble soil concentrations of each of these elements in the exposed and control samples from each location, the relative percent difference (RPD) between the exposed and the control concentrations, and the concentrations measured in filtered samples of the slurry (mean of three samples collected from different locations).

Table 4.1  Relative Percent Difference (RPD) in the soil concentration between the exposed and the control soils for elements that were elevated in the exposed soil.

| Sampling Location | U (mg kg-1) | Ca (mg kg-1) | Mg (mg kg-1) | Na (mg kg-1) | S (mg kg-1) |
| --- | --- | --- | --- | --- | --- |
| Acid plant |  |  |  |  |  |
| Control concentration | 445 | 550 | 320 | 30 | 773 |
| Exposed concentration | 10,250 | 870 | 330 | 50 | 949 |
| RPD (%) | 183 | 45 | 3 | 50 | 20 |
| Crushing transfer tower |  |  |  |  |  |
| Control concentration | 12,000 | 140 | 575 | 5 | 64 |
| Exposed concentration | 49,000 | 1,465 | 2,340 | 85 | 3,895 |
| RPD (%) | 121 | 165 | 121 | 178 | 194 |
| Mean slurry concentration (n=3) | 331 ± 49 | 352 ± 34 | 3780 ± 656 | 71 ± 11 | 25,233 ± 4,067 (as sulfate) |

##### Zone 1 Clearance

Given that RP2 water was used in the wash down process, all of the samples will exhibit baseline chemistry values that reflect RP2 water quality. This baseline was defined by analysing a sample taken directly from the water cart (J0269 Water Cart). The analyte concentrations measured in each sample were then corrected by subtracting the baseline values, as measured in the water cart sample. The resultant concentrations shown in Table 4.2 are assumed to represent the concentrations that would be present in rainwater runoff from the Zone 1 area. These concentrations are compared to the indicative water quality classes as described in ERA’s Water Management Plan (2013). In some samples some of the analyte concentrations were similar to the baseline RP2 concentrations. They are indicated in Table 4.2 by “RP2”.

Table 4.2  Corrected key filterable analyte concentrations in runoff from Zone 1.

| Sample No. | Location | EC µS cm-1 | pH | Mg mg L-1 | Mn mg L-1 | SO4 mg L-1 | U mg L-1 | 226Ra mBq L-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| JO263 | Site 1 (WS1) | 2320 | 7.55 | 91.0 | 14.3 | 486 | 0.07 | 4370 |
| JO264 | Site 2 (WS2) | 3910 | 5.14 | 361 | 83.1 | 1930 | 3.75 | 109 |
| JO265 | Site 3 (WS3) | 2730 | 6.28 | 157 | 19.2 | 845 | RP2 | 7600 |
| JO266 | Site 4 (WS4) | 2580 | 7.45 | 145 | 19.3 | 716 | 1.30 | 1900 |
| JO267 | Site 5 (WS5) | 2350 | 7.57 | 93.0 | 10.1 | 506 | 0.95 | 3860 |
| JO270 | RP2 central drain before release | 1790 | 8.69 | 15.0 | 2.24 | 96.0 | RP2 | 1691 |
| JO271 | RP2 central drain outflow | 2320 | 4.76 | 81.0 | 24.2 | 506 | 5.20 | 3472 |
| JO272 | RP2 central drain after release | 1670 | 9.70 | RP2 | RP2 | RP2 | RP2 | RP2 |
| JO273 | RP2 west drain after release | N/S | N/S | RP2 | 0.21 | RP2 | 0.27 | 409 |
| JO269 | Water Cart | 1660 | 8.79 | 188 | 0.0495 | 904 | 1.55 | 1691 |
| RP2 indicative water quality3 |  | 1870 | 8.36 | 230 | 0.20 | 1010 | 4.0 | 29401 |
| Process water indicative water quality3 |  | 26171 | 3.98 | 6219 | 2107 | 34528 | 24.0 | 135002 |

N/S – Not sampled

1. Mean percentage of filterable 226Ra in RP2 waters (Akber et al. 2011)

2. Mean percentage of filterable 226Ra in process water (EnRad unpublished data)

3  Indicative water quality class analyte concentrations (ERA 2013)

The analyte concentrations in the majority of the samples were either below, equal to or within two times the RP2 indicative water quality concentrations. The notable exception is dissolved Mn which was elevated compared to the RP2 indicative water quality concentration (0.2 mg L-1) in almost all samples. When comparing the surface runoff to RP2 water quality the difference in the respective matrices and the physico-chemistry needs to be taken into account. The pH of RP2 is around 8 and at this level Mn is typically present in oxidation states that readily adsorb to particulate material and bond with organic matter and oxides to form insoluble compounds, resulting in a reasonably low concentration of dissolved Mn. The source of the elevated concentrations in the runoff is caused by the pyrolusite (MnO2) used in the acid leaching process. Whilst the concentrations are increased compared to RP2 water the concentrations are generally 2–3 orders of magnitude less than the process water indicative water quality concentration (2 107 mg L-1). Statutory water quality monitoring records for RP2 show that dissolved Mn concentrations above 83.1 mg L-1 were recorded on 593 occasions between 1981 and 2014. Due to the dilution capacity of RP2 and rapid adsorption of Mn the water was of sufficient quality to report to RP2 and not effect a discernible change in concentration.

During the wash down process the volume of water used to wash down the same surface area between the sampling sites may have varied due to the spray angle of the water and the restriction of the water cart to the road surface and thus may be a cause of variability between samples.

The sample collected from Site 2 (J0264) was higher in Mg, Mn, SO4 and U compared to other samples. This was the first sample collected during the wash down process and it was collected after a comparatively small volume of water had been applied. As a result, the sample was particularly contaminated with the labile metals and precipitated solutes present in Zone 1 in the vicinity of the WS2. All other samples were collected after significantly larger volume had been applied and as such the concentrations were more diluted.

The sample collected at the central drain during the flushing process (J0271) showed higher concentrations of dissolved Mn and U than the sample collected prior to the flush (J0270). This suggests that during the flushing process some of the residual slurry, of low pH, was washed through the storm drain system and into RP2. However, the sample of RP2 water collected in the vicinity of the drain immediately after the flushing took place (J0272) resembled RP2 water, indicating that the storm drain was fully cleared of all slurry residue during the initial period of the flush.

##### Zone 2 Clearance

The concentrations of key analytes in samples collected from Zone 2 on 19 December 2013 are shown in Table 4.3.

Table 4.3  Key filterable analyte concentrations measured in pooled rainfall from Zone 2.

| Sample No. | Location | EC µS cm-1 | pH | Mg mg L-1 | Mn mg L-1 | SO4 mg L-1 | U mg L-1 | 226Ra mBq L-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| JO376 | Site 1 | N/S | N/S | 752 | 132 | 3450 | 2.13 | 3670 |
| JO377 | Site 2 | N/S | N/S | 1070 | 192 | 4870 | 2.41 | 3780 |
| JO379 | Site 3 | N/S | N/S | 910 | 162 | 4210 | 1.11 | 3610 |
| JO380 | Site 4 | N/S | N/S | 756 | 161 | 3820 | 2.34 | 2530 |
| JO381 | Site 5 | N/S | N/S | 1040 | 188 | 5070 | 3.10 | 4130 |
| JO382 | Site 6 | N/S | N/S | 1970 | 525 | 10100 | 9.25 | 4810 |
| RP2 indicative water quality3 |  | 1870 | 8.36 | 230 | 0.2 | 1010 | 4.0 | 29401 |
| Process water indicative water quality3 |  | 26171 | 3.98 | 6219 | 2107 | 34528 | 24.0 | 135002 |

N/S – Not sampled

1. Mean percentage of filterable 226Ra in RP2 waters (Akber et al. 2011)

2. Mean percentage of filterable 226Ra in process water (EnRad unpublished data)

3  Indicative water quality class analyte concentrations (ERA 2013)

The results show that the concentration of most analytes in the Zone 2 samples were above the RP2 indicative water quality concentrations and substantially lower than the process water indicative water quality concentrations. The exception was U which was present in concentrations lower than the RP2 indicative concentration of 4.0 mg L-1 in all samples apart from Site 6 (J0382). This sample was located closest to the failed tank within Zone 2 and contained higher concentrations of all analytes. Statutory water quality monitoring records for RP2 show that dissolved U concentrations above 9.25 mg L-1 were recorded on 18 occasions between 2002 and 2003, ranging from 9.30 mg L-1 in 2002 to 14.3 mg L-1 in 2000. Due to the dilution capacity of RP2 and rapid adsorption of U the water was of sufficient quality to report to RP2 and not effect a discernible change in concentration.

It is likely that the Zone 2 concentrations are higher than the Zone 1 concentrations due to the fact that the standing rainwater pools would have had a longer contact time with the soil compared to the water truck method used in the Zone 1 sampling, where the contact time was relatively short. Furthermore, any solutes mobilised during the rainfall events preceding the sampling of Zone 2 would be flushed into and may also be evapoconcentrated over time in the sitting pools from which the samples were collected. It should also be noted that the majority of the Zone 1 area was sealed road surfaces, while Zone 2 was primarily earthen hardstand.

##### Zone 3 Clearance

The chemistry analysis results for the sampling of Zone 3 are shown in Table 4.4 along with the results from ERA’s monitoring of Zone 3 and indicative water quality classes.

Table 4.4  Key analyte concentrations measured in pooled rainfall from Zone 3.

| Location | EC µS cm-1 | pH | Mg_F mg L-1 | Mn_F mg L-1 | SO4_F mg L-1 | U_F mg L-1 | Ra_F mBq L-1 | Ra_T mBq L-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ERA–Zone 3 | 1330 | 8.32 | 114 | 0.028 | 608 | 5.75 | NR | 830 |
| SSD–Zone 3 | N/S | N/S | 114 | 0.027 | 606 | 6.20 | 694 | 891 |
| RP2 indicative water quality3 | 1870 | 8.36 | 230 | 0.20 | 1010 | 4.00 | 2940 | 32731 |
| Process Water indicative water quality3 | 26171 | 3.98 | 6219 | 2107 | 34528 | 24.0 | N/S | 143562 |

N/S – Not sampled

1. Mean percentage of filterable 226Ra in RP2 waters (Akber et al. 2011)

2. Mean percentage of filterable 226Ra in process water (EnRad unpublished data)

3  Indicative water quality class analyte concentrations (ERA 2013)

There was a single standing pool of water within Zone 3, which was sampled by both SSD and ERA. Results of analyte concentrations were compared to the indicative water quality of pond water (RP2) and process water classes.

The filterable and total (filterable + residual) 226Ra activity concentrations were substantially less than the RP2 indicative water quality values.

The filterable U concentration was recorded at a maximum of 6.2 mg L-1, above the RP2 indicative water quality value of 4.0 mg L-1. Statutory water quality monitoring records for RP2 show that dissolved U concentrations above 6.2 mg L-1 were recorded on 81 occasions between 1989 and 2013, ranging from 6.21 mg L-1 in 2005 to 14.3 mg L-1 in 2000. With the dilution capacity of RP2 and rapid adsorption of U onto suspended sediments the water was of sufficient quality to report to RP2 and not effect a discernible change in concentration.

The filterable concentrations of all other analytes in Table 4.4 were below the RP2 indicative water quality concentrations indicating that the clean up works within the bunded area of Zone 3 were sufficient to be of pond water quality.

##### Conclusions

The results of the sampling carried out during the cleanup activities for each zone show that contaminant concentrations in surface runoff from the spill were below process water quality and fell within the previously observed range of pond water quality.

Regardless, when the dilution and the neutralisation capacity of RP2 are taken into account, the concentration of dissolved contaminants in the surface runoff from the spill area will reduce rapidly as the runoff enters RP2. The high pH of RP2 waters will encourage the formation of insoluble inorganics (oxides and hydroxides) and the binding of metals to fulvic acids. The alkalinity of RP2 water will also neutralise the acidity associated with the slurry.

Based on the results shown above for each of the cleanup activities, the Supervising Scientist was satisfied that each of the zones had been sufficiently cleaned to return this area to the pond water circuit and advised the NT DME accordingly. This was supported by ongoing monitoring of RP2 which showed no observable impact attributable to the leach tank spill.

### 4.1.3  Offsite surface water

#### 4.1.3.1  Magela Creek chemistry

Flow was first recorded at the Magela Creek upstream and downstream monitoring stations on 28 November 2013 and SSD then commenced its 2013–14 wet season monitoring program, which is comprised of continuous in-situ measurement of EC, pH and turbidity and automated sample collection based on EC and turbidity levels.

The leach tank failure occurred on the recessional tail of a peak in Magela Creek water level related to a 69 mm rainfall event recorded on 6 December 2013. During the 15 day period following the incident there were no significant flow events in Magela Creek and the EC at the upstream (MCUGT) and downstream (MCDW) sites stabilised at approximately 18 µS cm-1 and 20 µS cm-1, respectively (Figure 4.10).

Figure 4.10  Continuous EC data for Magela Creek from 28 November 2013–25 June 2013. 
SSD data.

The upstream and downstream pH also stabilised at approximately 5.75 (Figure 4.11). The coincident behaviour and the similar values measured at the upstream and the downstream sites for both pH and EC indicate that there was no effect from the leach tank failure on Magela Creek physico-chemistry during this period. This is unsurprising as there was no rainfall during this period and, hence, no transport mechanism enabling export of contaminants from the mine site to Magela Creek.

Figure 4.11  Continuous pH data for Magela Creek from 28 November 2013–30 December 2013 (SSD data). The pH trigger values are provided for information only as these trigger values were determined statistically from historical weekly grab sampling data, and only apply to water quality measured in grab samples.

From 22 December 2013 flow within Magela Creek increased due to a number of rainfall events. During this period the EC was inversely related to water level, which is typical of the Magela Creek system. The rainfall dilution and hydrodynamic damming of backflow billabongs results in decreased EC during high flows and increased EC during low flows, when the billabong waters (particularly Coonjimba and Georgetown Billabongs) flush into Magela Creek as the water level recedes (Figure 4.10). A similar trend is observed in pH (Figure 4.11).

Following the peak of flow on 6 December 2013 the turbidity decreased to below 5 NTU. Turbidity and creek flow remained low until 23 December 2013 after which there were a number of coincident turbidity peaks at both the upstream and downstream sites in relation to the water level variation (Figure 4.12). This is typical turbidity behaviour in Magela Creek and indicates that the source of the turbidity measured at the downstream site is from upstream of the mine.

Figure 4.12  SSD continuous turbidity data for Magela Creek from 28 November 2013–15 July 2014. The turbidity trigger values are provided for information only as these trigger values were determined statistically from historical weekly grab sampling data, and only apply to water quality measured in grab samples.

The total U concentrations measured in grab samples and automated samples collected from Magela Creek are shown in Figure 4.13, the total Mn concentrations in Figure 4.14 and the total Mg concentrations in Figure 4.15. Each figure also shows the continuous EC measured at the upstream and downstream sites. Prior to the incident and in the weeks following, the total U concentrations remained below the toxicity-derived Focus trigger value of 0.3 µg L-1 and well within the range of what is typically measured in Magela Creek. This is also true for total Mn concentrations with the exception of a sample taken during the first flush period that had a total Mn concentration of 44 µg L-1 (Figure 4.14). The toxicity-derived manganese guideline of 75 µg L-1 only applies when the creek discharge is greater than 5 m3 s-1 when flow in the creek is dominated by surface flow and not Mn-rich groundwaters. At the time of sample collection creek flow was < 3.5 m3 s-1 and thus the trigger values are not relevant.

The total Mg concentrations measured at the downstream site remained below the Focus trigger value of 1 mg L-1 with the exception of a sample triggered during the EC peak on 23 December 2013, which had a total Mg concentration of 1.7 mg L-1 (Figure 4.15). The source of the elevated Mg and EC is likely to be from the backflow billabongs, Georgetown and Coonjimba, which flush into Magela Creek as the water level recedes. The magnitude and timing of these events is in accordance with that observed over previous wet seasons.

Figure 4.13  SSD uranium concentration data and continuous EC for Magela Creek from 
28 November 2013–15 July 2014. SSD data.

Figure 4.14  SSD manganese concentration data and continuous EC for Magela Creek from 
28 November 2013–15 July 2014. SSD data.

Figure 4.15 SSD magnesium concentration data and continuous EC for Magela Creek for 28 November 2013–15 July 2014

Surface water grab samples are collected fortnightly from Magela Creek upstream and downstream of the Ranger mine. Two fortnightly samples are combined to give monthly composite samples. Total 226Ra is measured in these samples and results for the 2013–14 wet season can be compared with previous data ranging back to the 2001–02 wet season (Figure 4.16). The sample results for 2013–14 were within the historic range observed in Magela Creek since 2001.

During 7–13 December 2014 six 226Ra samples were collected at both the upstream and downstream monitoring sites in response to the leach tank incident and analysed individually. A routine composite sample was not obtained during this time. Consequently the average 226Ra activity concentration of these samples has been included as a proxy composite sample for December 2014 and used in the calculation of the 2013–14 wet season median difference.

Since 2010, 226Ra analyses of a composite of samples collected by autosampler during individual EC-triggered events have also been performed. There was one EC-triggered event sample analysed for 226Ra during the 2013–14 wet season. This sample is a composite of five samples collected during an EC event on 15–16 May 2014. The result is shown in Figure 4.15, together with the results from the incident sampling and routine radium analyses. The EC-triggered event data are not included in the calculation of the wet season median difference, because these EC events are short-lived and their impact on seasonal 226Ra loads is very small.

The data from monthly sample composites show that the levels of 226Ra are very low in Magela Creek, both upstream and downstream of the Ranger mine. An anomalous 226Ra activity concentration of 8.8 mBq L-1 measured in a sample collected from the control site upstream of Ranger in 2005 was probably due to a higher contribution of 226Ra-rich soil or finer sediments that are present naturally in Magela Creek. This has previously been discussed in the 2004–05 Supervising Scientist’s annual report.

Figure 4.16  226Ra in Magela Creek 2001–2014

The limit value for total 226Ra activity concentrations in Magela Creek has been defined for human radiological protection purposes, and is based on the median difference between upstream and downstream 226Ra activity concentrations over one entire wet season (Iles 2004). The median of the upstream 226Ra data collected over the current wet season is subtracted from the median of the downstream data. This difference value, called the wet season median difference, quantifies any increase at the downstream site, and should not exceed 10 mBq L-1.

A wet season median difference of 10 mBq L-1 would result in a mine origin ingestion dose from 226Ra bioaccumulated in mussels of about 0.3 mSv, if 2 kg of mussels were ingested by a 10 year old child. Wet season median differences (shown by the horizontal lines in Figure 4.16) from 2001 to 2014 are close to zero, indicating that the great majority of 226Ra is coming from natural sources of 226Ra located in the catchment upstream of the mine. The wet season median difference for the entire historical monitoring period (2001–14) is 0.1 mBq L-1.

The wet season median difference for the 2013–14 wet season is 0.5 mBq L-1, indicating a slightly higher median 226Ra value for the downstream monitoring site than for the upstream monitoring site. This result is approximately 5% of the 10 mBq L Limit and is only marginally increased compared to the range of variation observed in previous years. The individual sample results for 2013–14 were well within the magnitude and range of variation of historic results. Although this is the greatest wet season median difference since 2001 the result for 2013–14 is not of environmental significance and SSD do not believe that this is attributable to the incident.

##### Conclusions

Results of surface water chemistry monitoring conducted by SSD in Magela Creek demonstrate that there were no unusual increases in general parameters or chemical analytes following the incident.  It is concluded that there was no environmental impact to the downstream aquatic environment associated with the leach tank incident.

#### 4.1.3.2  Magela Creek in situ toxicology testing

Flow was first recorded at the Magela Creek upstream and downstream monitoring stations on 28 November 2013. The first of 12 tests in Magela Creek commenced on the 5th December 2013, seven days after the establishment of continuous flow. The leach tank failure that occurred on 7 December 2013 thus coincided with the first test in Magela Creek. Following the incident, three more weekly tests in Magela Creek followed before the commencement of the first of nine Gulungul tests (9 January 2014). Thereafter, the Magela tests alternated weekly with Gulungul tests. The final test was completed in Magela Creek on 28 April 2014. Upstream and downstream egg production and difference values for Magela Creeks are displayed in Figure 4.17.

Figure 4.17 Time-series of snail egg production data from toxicity monitoring tests conducted in 
Magela Creek. The time of the incident is denoted within the figure by the vertical red line

The negative mean difference value for the twelve 2013–14 wet season tests indicating higher downstream egg production than upstream is consistent with the historical trend of greater downstream egg production. ANOVA results for the 2013–14 wet season tests, together with results from previous wet seasons, are displayed in Table 4.5. The significant difference observed in the 2009–10 wet season, associated with particularly high egg production at the downstream site relative to the upstream site, is discussed in the 2009–10 Supervising Scientist Annual Report. No significant difference has been observed between the 2013–14 wet season tests and those from previous wet seasons (Table 4.5).

In the previous (2012–13) wet season, a marked increase in overall egg production was observed compared to the previous five wet seasons. This above-average increase in egg production continued in both creeks in the 2013–14 wet season (Figure 4.16). A significant factor contributing to this appears to be a more effective culturing regime for the snails at the laboratory aquaculture facility as discussed in the 2012–13 Supervising Scientist Annual Report (Sections 3.2.3.2 and 4.4).

These results show no unusual response from the snail tests conducted post-spill and support the conclusions of the physico-chemical monitoring that there have been no offsite environmental impacts from the spill.

Table 4.5  Results of ANOVA testing comparing Magela upstream-downstream difference values for mean snail egg number for different ‘before versus after’ wet season scenarios.

| Before | After | Probability value (P) | Statistical Significance |
| --- | --- | --- | --- |
| All previous seasons | 2009-10 | 0.043 | at 5% level |
| All previous seasons | 2010-11 | 0.436 | NS1 |
| All previous seasons | 2011-12 | 0.916 | NS |
| All previous seasons | 2012-13 | 0.083 | NS |
| All previous seasons | 2013-14 | 0.865 | NS |

1 NS: Not significant

## 4.2  Ground Water

### 4.2.1  Onsite soil profiling

#### 4.2.1.1  Soil characterisation

The five soil profiles obtained (Section 3.3.1) contained very poorly sorted soil and other material, which ranged in size from very fine grained (< 0.2 mm diameter) to very coarse and pebble-sized (> 63 mm diameter). Grain composition was heterogeneous and included an abundance of fine-grained silt and clay, as well as coarser bitumen, quartz, quartzite, and metamorphic clasts. Ferruginous (iron-rich) nodules were common. Porosity was rarely identified, with the exception of Hole 3 where, from 0.25–0.35 m depth, occasional 0.5 mm diameter pores were found present. All holes showed similarities in their grain sizes, and therefore are likely to have similar permeability. Only Hole 5 may have a greater permeability in the uppermost horizon, which contains dense grass roots as well as gravels.

The soil was highly compacted and consolidated in parts. Peds were often aggregated, however often broke down when a weak force was applied suggesting they were not always tightly bound. Some cementation had occurred of the finer-grained clays between the coarser clasts. In addition to this, some profiles contained a layer of bitumen (possibly former road-base), which further increases the density and compaction. The most unconsolidated soils were found at Hole 5, due mostly to some organic matter in the soil at the surface. In all holes, at a depth of approximately 1 m, weathered bedrock was thought to be encountered, as the material was extremely dense and difficult to extract beyond this depth.

Soil colour can be used to infer information about the soil composition and chemistry. Soil colour notation follows the “Munsell® Soil Colour Charts” (Anon 1975) and uses the Hue, Value, Chroma system. Hue notation indicates the sample’s relation to Red, Yellow, Green, Blue and Purple; Value indicates its lightness; and Chroma indicates its strength (Anon 1975). Overall the soils showed a large variation in colours and included mostly blacks, greys, reds, yellows and browns. However, overall a general pattern in all profiles of lighter grey brown at the surface, underlain by a grey/black coarse grained horizon at approximately 0.1–0.5 m in the middle of the profiles, underlain by yellows, browns and deeper reds in the lowermost horizons. In Hole 1, the grey/black coarse grained horizon intersects the surface and does not have an uppermost brown horizon as the other holes do. The abundance of red soils and the presence of ferruginised nodules indicate a high concentration of iron. Figures 4.18–4.22 show the soil profiles for each hole, with the exception of Hole 2 which was excavated by auger.

Figure 4.18  Sediment sampling Hole 1.

Figure 4.19   Auger mounted on a bobcat used to drill Hole 2.

Figure 4.20  Sediment sampling Hole 3.

Figure 4.21  Sediment sampling Hole 4.

Figure 4.22  Sediment sampling Hole 5.

The five holes dug in the Ranger plant area for this investigation consisted of a variable surficial layer of fill overlying in situ lateritic soil material. The origin of the fill and the exact time of its placement are not known. The buried lateritic soils correspond to the red and yellow earths described in previous studies (Chartres et al. 1991). However, some stripping of the A horizon material may have occurred before burial with fill and there is an additional abundance of anthropogenic mine site material. The fill comprised bitumen, road base, blue metal/cracker dust and what is interpreted to be dust from the conveyor belt supplying the processing plant (in Hole 5). The fill material was often compacted and had low permeability. Due to the low permeability of the surficial materials in the area of the spill, it is unlikely a large amount of infiltration of leachate occurred, particularly because of the short residence time at the surface as the majority of the slurry was cleaned up within a few days of the spill. The most permeable material is in the area of Hole 5 where the surface contains grass and, although the site of hole 5 was unaffected, similar grassy sites that were inundated with slurry may have experienced some infiltration of contaminated liquor.

Radiation measurements were taken for each of the soil horizons at each site. Activity profiles for holes 1, 3, 4 and 5 were measured with an Automess α/β/γ surface contamination probe (model: 6150 AD-17) with a measuring range of 0.1-10,000 s-1, connected to an Automess meter (model: 6150 AD 5/H). The probe was calibrated by the Queensland University of Technology Radiological Laboratory in December 2011. Soil samples were poured into aluminium containers and the probe was placed immediately on top of the material, without touching the soil, and the counts per second were measured and noted down for each sample. The results are shown in Figure 4.23. This figure shows that while radiation values are low for most horizons at each site (< 2 cps), the second horizon of hole 5 is greater, being approximately 20 cps. Because this site was not affected by the spill, this is not a response feature and most likely a function of mine site dust accumulation from the overhead conveyor.

Figure 4.23  Depth profiles of radiation levels for Holes 1, 3, 4 and 5. Because Hole 2 was sampled with an auger, no profile image is available.

#### 4.2.1.2 Soil chemistry

The general chemical composition of the soil profiles in Holes 1, 3, 4 and 5 were characterised by analysing samples from each layer for water and acid extractable concentrations of 65 elements. The water extraction gives an indication of the elements that are readily dissolvable and could potentially become remobilised during rainfall events and transported either in surface run-off to other areas in the catchment, or in soil infiltration towards the groundwater. The acid extraction gives some information on the mineralogical composition of the soils and provides a means of comparing the data collected during this investigation to historical data collected by others. The data from each of the layers were combined and averaged for depth ranges 0–10 cm, 10–50 cm and 50–100 cm for each hole. Any concentrations that were less than five times the analytical detection limit have not been reported.

The element concentrations in the exposed soils (Holes 1 and 3) were compared to the concentrations in the control soils (Holes 4 and 5) to determine if there was any significant residual contamination in the slurry exposed area. Figures 4.24 and 4.25 show the distribution of each element as a relative percentage difference (RPD) between the control soils and the exposed soils for the water extraction and the acid extraction, respectively. An RPD of 0% indicates uniformity between the control and the exposed soils, an RPD > 0% indicates that the concentrations were more elevated in the exposed soils and an RPD < 0% indicates that the concentrations were more elevated in the control soil.

Figure 4.24  Comparison of water extractable concentrations in control and exposed soils at different depths.

The water extractable concentrations of a number of elements were elevated in the exposed soils compared to the control soils. Of the 8 elements that were elevated in the exposed soils at the 0–10 cm depth range, strontium was particularly high, with an RPD of 189%, and manganese and calcium were also over 80% higher than the control soils. Twenty one elements were elevated in the exposed soils in 10–50 cm depth range. Manganese and uranium were the only elements that were elevated in the exposed soils at the 50–100 cm depth range. All other elements were present in greater water extractable concentrations in the control soils at depth. Copper, magnesium and zinc were present in higher concentrations in the control soils at all depths.

Figure 4.25  Comparison of acid extractable concentrations in control and exposed soils at different depths.

As with the water extractable concentrations above, the 10–50 cm depth range contained the highest number of acid extractable elements that were elevated compared to the control soils, with barium, strontium and manganese concentrations being the most significantly elevated compared to the controls. The high mean concentrations of the elements in the top 50 cm of the exposed soils was attributed mainly to the elevated concentrations measured in Hole 1 soils, which were much higher than those measured in the other exposed soils from Hole 3. The top 10 cm at Hole 1 was classified as black bitumen and mixed black gravel fill (Figure 4.18). It is possible that a number of the trace elements were extracted from the bitumen or road surface itself, rather than residual slurry. The highest manganese concentrations were measured in Hole 1, with a mean of 35 650 mg kg-1 in the top 10 cm. The mean concentration of manganese in the top 10 cm of Hole 3 (the other exposed site) was only 412 mg kg-1. It is likely that the elevated manganese in Hole 1 was present due to contamination of the soil from the pyrolusite (MnO2) stockpile in the same location (Hollingsworth 2006). Hollingsworth (2006) reported a total manganese concentration (acid extractable) of 159 400 mg kg-1 in a surface soil sample collected in the vicinity of the pyrolusite stockpile, indicating that it is a major source of manganese contamination. The analytical suite analysed by Hollingsworth (2006) was not as extensive as this investigation, so it is possible that a number of the other elements that were elevated in the surface soils of Hole 1 can be attributed to the pyrolsulite stockpile but have not previously been identified or reported. The acid extractable uranium concentrations were higher in the control soils for all depth ranges, as was the case for a number of other elements.

There was a general trend in decreasing concentrations of both water and acid extractable elements down the soil profile, with higher concentrations measured in the surface soils and lower concentrations measured at depth. The exceptions to this were calcium, sodium, sulphate, chromium, caesium, iron, rhenium, scandium, vanadium, zirconium, which were elevated in the 50–100 cm depth range for control Hole 5. Some of these elements were also slightly elevated at depth in the exposed holes but the concentrations were within the ranges measured in the control holes.

The elements that were elevated in the exposed soils included some common mine site contaminants (Mn, Pb, Ca, SO4 and Ni) as well as some trace elements, all of which are likely to be associated with either the mineralogical composition of the Ranger ore and associated waste rock or anthropogenic sources such as bitumen and concrete (Office of the Supervising Scientist 2002). These elements are summarised in Table 4.6, showing the mean concentrations measured in the water extraction solutions (1:20 soil to water) at each depth range along with the concentrations measured in the slurry and the indicative RP2 concentrations, where available.

The data in Table 4.6 show that the residual water soluble concentrations of the elements that were elevated in the exposed soils were extremely low compared to the dissolved concentrations measured in the slurry itself.  Most of the elements were at least one order of magnitude lower in the water digest solution compared to the slurry concentrations, with the exception of barium and strontium which had water soluble concentrations in the top 10 cm of hole 1 that were similar to slurry concentrations (80.3 µg L-1) and of 482 µg L-1, respectively).

Table 4.6  Mean exposed water extractable concentrations for elements that were elevated in exposed soils compared to control soils, along with the mean dissolved concentrations measured in the slurry and the RP2 indicative water quality concentrations, where available.

| Element (µg L-1) | Soil depth range |  |  | Slurry concentration (n = 3) | RP2 Indicative water quality concentration |
| --- | --- | --- | --- | --- | --- |
|  | 0–10 cm (n = 3) | 10–50 cm (n = 6) | 50–100 cm (n = 4) |  |  |
| Al (mg L-1) | 4 | 2 | 0.02 | 1044 |  |
| Ba | 53.6 | 23.3 | 6.5 | 81.5 |  |
| Ca (mg L-1) | 5.0 | 4.8 | 0.7 | 352 |  |
| Ce | 9.4 | 4.6 | 0.1 | 709 |  |
| Co | 4.1 | 3.5 | 0.1 | 4427 |  |
| Cr | 8.8 | 12.5 | 1.0 | 1260 |  |
| Cs | 0.9 | 1.2 | 0.1 | 23.4 |  |
| Fe (mg L-1) | 1.6 | 0.77 | 0.03 | 380 |  |
| Ga | 5.1 | 4.8 | 0.1 | 24.3 |  |
| K (mg L-1) | 1.9 | 2.4 | 0.3 | 59.3 |  |
| La | 6.0 | 2.3 | 0.1 | 173 |  |
| Li | 3.4 | 2.3 | 0.5 | 3193 |  |
| Mn (mg L-1) | 0.31 | 0.04 | 0.01 | 1091 | 0.2 |
| Nd | 3.0 | 1.6 | 0.1 | 553 |  |
| Ni | 16.6 | 13.4 | 0.2 | 4800 |  |
| Pb | 9.9 | 6.2 | 0.1 | 1233 |  |
| Rb | 7.2 | 7.5 | 1.7 | 278 |  |
| Si (mg L-1) | 5.3 | 5.7 | 0.4 | 297 |  |
| S (mg L-1) | 7.4 | 2.7 | 2.0 | 25233 | 1010 |
| Sr | 244 | 8.6 | 2.1 | 532 |  |
| Th | 2.4 | 1.8 | 0.1 | 425 |  |
| Ti | 66.3 | 39.2 | 5.0 | 100 |  |
| U (mg L-1) | 0.03 | 0.03 | 0.0003 | 331 | 4 |
| V | 11.5 | 13.4 | 0.5 | 463 |  |
| Y | 1.4 | 1.5 | 0.1 | 4483 |  |
| Zr | 9.3 | 10.6 | 0.5 | 8.1 |  |

The elevation of Ba and Sr in the profiles is difficult to interpret, as available Ba and Sr species form the acid slurry would be likely to form insoluble inorganic sulphate salts as the pH conditions neared natural with dilution and flushing of the site. These data may indicate a slurry-related signal, however barium and strontium are the only elements that show this trend. Many of the other contaminants that were highly elevated in the slurry were very low in the water extraction solutions, showing that even though the elements were elevated in the exposed soils compared to the controls, the exposed soils have not become a significant source on contaminants to the catchment area. The comparison of the water extraction solution concentrations to RP2 indicative water quality concentrations indicates that there is very little potential for groundwater infiltration from the exposed soils to impact RP2 water quality.

Previous investigations of soil chemistry in the plant area have shown that the soils are contaminated with Cu, Pb, Zn, Mn and U (Hollingsworth 2006, Alarcon Leon et al. 2007a). These studies attribute the source of contamination to general plant-related processes, which is important because it affects the baseline chemistry against which to assess potential slurry contamination. This background contamination explains why so many elements were elevated in the control soils and it introduces ambiguity in determining the source of specific elements within the complex soil composition. The potential sources materials in the vicinity of the slurry spill area includes anthropogenic material such as bitumen and concrete, existing contaminated soils and mine waste rock that has been used to infill the area. The relative contributions of elements from any of these sources is complex to characterise because their geochemical characteristics vary widely.

Overall, the chemistry results have shown that some elements were elevated in the exposed soils compared to the control soils and that a number of these elements were present in water and acid soluble compounds. However the potential for the exposed soils to leach high concentrations of water soluble elements during rainfall was low. The majority of water and acid soluble elements were restricted to the top 50 cm of the soil profile and there was no conclusive evidence to show that infiltration of slurry leachate occurred at lower depths.

Soil sampling within the mine footprint has not occurred since the studies undertaken by Hollingsworth (2006) and Alarcon Leon et al. (2007a). This presents a knowledge gap as possible changes in contamination levels over the last seven years have not been quantified. It is recommended that soil contamination investigation works be revisited to better inform site closure planning.

### 4.2.2  Groundwater impact assessment by Geoscience Australia

This Section provides a brief overview of the Geoscience Australia report and contains information on: (1) Plant area surface materials; (2) Plant area hydrogeology; (3) Hydrogeochemical impact analysis; and (4) Conclusions. The full report is attached at Appendix A.

#### Plant area surface materials

The area of the plant which was exposed to the leach tank spill is characterised by a mixture of natural and artificial sealed and unsealed surfaces. These were investigated in detail by the Supervising Scientist and have been described in Section 4.2.1. Infiltration will depend largely on the hydraulic conductivity of the materials at the surface, which relates to the permeability of the sediment and is a measure of how well fluid is able to move through any pore spaces. The chemistry of the surficial material must also be understood as some water-rock interactions are able to immobilise the flow of contaminants in a plume.

Due to the compacted nature of the sealed surfaces, they are likely to have facilitated runoff, with low possibility of infiltration, as shown in Section 4.2.1. Unsealed and vegetated surfaces are most likely to be areas of potential contaminant infiltration, because of potentially greater hydraulic conductivities. However, most of the unsealed areas within the spill extent are heavily trafficked, subject to significant compaction and likely of generally similar infiltration properties to the sealed areas.

Soil contamination mapping in the vicinity of the plant area was undertaken by Hollingsworth (2006). This study examined profiles up to 1 m depth, taking samples at various intervals. Two sites are located adjacent to the leach tanks, and provide data on pre-spill impacts. These had slightly acidic to neutral pH, a wide range of EC in the upper ranges of the site-wide baseline, and high trace metals with reference to the Ranger site-wide average baseline.

#### Plant area hydrogeology

Background information provided by GA shows that the Ranger mine encompasses three local groundwater catchments: the Coonjimba, Djalkmara and Corridor Creek catchments. Four aquifers are identified on site (Weaver et al. 2010): Aquifer 1a (shallow alluvial sediments); Aquifer 1b (weathered rock); Aquifer 2 (weathered rock); and Aquifer 3 (fractured rock). The current conceptual understanding of hydrogeology at Ranger (Puhalovich 2010, Weaver et al. 2010, Golder Associates Pty Ltd 2011) is refined from that of Salama and Foley (1997), in that it recognises the importance of rock weathering variability as a critical determinant of the aquifer properties, including hydraulic conductivity. Groundwater flow through the Ranger mine site more broadly can be split into a shallow flow system and a deep flow system.

In the plant area, the spill extent is interpreted to overlie aquifers 1b and 2, characterised by the upper part of the weathered profile grading down in parts to weathered bedrock, with clay and iron-rich sediments present. These sediments host the water table during the wet season. Groundwater flow occurs either within a porous or fractured-porous medium.

#### Groundwater levels and groundwater flow

Assessing the spatial and temporal variation of groundwater levels aids the understanding of movement of groundwater in the area. A previous study by Alarcon Leon et al. (2007a) of groundwater flow in the plant area showed that the water table fluctuates significantly between the wet and dry season, rising by up to 5 m in the wet; and that there is a local groundwater flow divide almost directly underlying the plant area which directs groundwater to the south, towards Corridor Creek and Pit 1, or to the north, towards RP2 and Pit #3. In addition to this, GA undertook an interpretation of groundwater flow using more widespread and recent water-level data. Their methodology assessed groundwater level data as a temporal average for different periods over the plant site. This was necessary as a result of the limited number of concurrent data points in a suite of bores for any specific month, particularly during recent years. Long-term wet (Figure 4.25) and dry (Figure 4.26) season average groundwater maps are included below.

The results from the water-level assessment show that there is a persistent groundwater divide located beneath the plant site causing groundwater to flow from the plant area in a north-northwest direction towards RP2 and in a south-southeast direction towards Corridor Creek. There may be subtle variations in flow directions over time, but the general trend in a northerly and southerly direction remains consistent over time. The breadth of the groundwater flow divide changes with each season and the subsequent gradients in flow change also.

Figure 4.25  Long-term average of wet season water-level records. Bores with fewer than 100 records have been labelled with the number of records available. Arrows indicate the direction of groundwater flow. Image courtesy of Geoscience Australia.

Figure 4.26  Long-term average of dry season water-level records. Bores with fewer than 100 records have been labelled with the number of records available. Arrows indicate general direction of groundwater flow. Image courtesy of Geoscience Australia.

Hydrogeological work undertaken across the Ranger site has identified that faulting and shearing play an important role in site groundwater flow regimes. In some cases, faults may act to compartmentalise groundwater systems, isolating some parts from others. In other cases, faults will provide conduits for flow. Detailed structural mapping data and fault hydrogeological parameters are not available in the plant area or in the Corridor Creek catchment but a major north-trending fault offsets geological units approximately 400 m to the west of Leach Tank 1. With creek baseflow potentially contributing to the groundwater balance, it is important to understand the role that faults play in driving groundwater flow, inter-aquifer connectivity and surface water—groundwater connectivity.

The nearest surface water receptor to the site of the spill is Corridor Creek, which flows to the south of Pit 1 in an easterly direction, into Magela Creek approximately 750 m east of Leach Tank 1. GC2 is a surface water gauging structure installed downstream of Pit 1 on Corridor Creek. Daily discharge data from GC2 for the period from July 2010 through to the end of February 2014 shows distinct peaks in flow during the wet season, with possible low to moderate baseflow contributions identified during the dry season of 2011, mid-June to mid-August 2012, and mid-April to the end of June 2013 (Figure 4.27).  These events are shown by flow above zero without corresponding rainfall events. The regular and defined baseflow events indicate that Corridor Creek is likely to be receiving some portion of flow from interaction with groundwater, although much of this is due to the ongoing release of treated waters upstream in the catchment.

Figure 4.27  Rainfall compared to GC2 discharge from July 2010 to February 2014 (rainfall data from BoM 2014; GC2 discharge volumes supplied by ERA). Image courtesy of Geoscience Australia.

#### Plant area hydrogeochemistry

An earlier study of potentially contaminated groundwater was undertaken between 2006 and 2009 in the processing plant area (Alarcon Leon et al. 2007a; Alarcon Leon et al. 2007b; Gellert 2009, Gellert & Jones 2008). Alarcon Leon et al. (2007b) concluded that groundwater underlying the plant area is contaminated with trace metals and sulfate. This was correlated with low groundwater pH and the plant area was identified as a source for groundwater contamination. Three contamination plumes were identified:

Low pH, high Fe, U and SO4 sourced from the Counter Current Decantation (CCD) circuit and moving along the southerly flow path.

Enriched in SO4, Fe, Mn and U and moving along the northerly flow path from the Acid Plant and Sulfur Stockpile zone.

A plume associated with weak enrichment in total petroleum hydrocarbon fractions, moving easterly from the diesel tanks during the dry season.

Work by Gellert (2009) showed that contaminant plumes were moving extremely slowly. They had not progressed measurably between 2006 and 2009. No samples have been collected after 2009 with which to further verify transport rates. It is likely that any contamination from the spill would move at a similar rate.

ERA (ERA 2013) state that the groundwater monitoring program for Ranger within the Corridor Creek Catchment is set up to identify potential impacts from process water seepage from Pit 1, as well as from the Corridor Creek Land Application Area (which lies to the south of Pit 1, in the headwaters of Corridor Creek) and that contamination from the plant area, and its potential impacts, are not part of the routine groundwater monitoring program at Ranger.

It order to add more information to previous work, and to assess recent data, including post-spill data where available, GA undertook an analysis of hydrogeochemistry in the plant area. An average groundwater sulfate map (Figure 4.28) highlights the extent of contamination at the site prior to the date of the spill. Additionally a pH map was produced to gain a better understanding of the current extent of groundwater contamination while a HCO3 map was produced to gain an understanding of potential buffering capacity for the uncontaminated groundwater which may be exposed to contaminant fluid. These maps and all results can be found in Appendix A.

It is evident from the results that pre-existing contamination occurs under the plant area, however due to the slow moving nature of this plume it is considered an issue to be addressed during site remediation. The sulfate concentrations range from below detection limit in the south-southeast and northeast of the plant area to approximately 12 000 mg L-1 under the lime towers. It is still unclear what the source of the contamination may be, but this mapping is consistent with other work, which showed that sulfate plumes extend towards the northwest and south-southeast of the plant area and remain slow moving (Alarcon Leon et al. 2007a, Gellert 2009, Gellert & Jones 2008).

Individual bores were assessed to characterise the hydrogeochemistry of groundwater in the vicinity of Leach Tank 1 prior to the spill. Figure 4.29 and Figure 4.30 show Stiff Diagrams giving the groundwater composition of Bores 35 and 36 pre- and post- spill, respectively. Although the concentrations are almost an order of magnitude higher in comparison to 2009, the water type is still magnesium-sulfate (Mg/SO4) dominant, with sodium and potassium (Na + K) being a secondary cation component.

Figure 4.28  Natural neighbour interpolated surface of average SO4 concentrations in groundwater between 2006 and 2013. Labelled bores are used for more detailed analysis. Image courtesy of Geoscience Australia.

Figure 4.29  Stiff Diagram from bores 35 and 36 on 15/01/2009 showing Mg/SO4 and Na+K/SO4 water types. (Image courtesy of Geoscience Australia).

Figure 4.30  Stiff Diagrams from bores 35 and 36 post-spill composition. Image courtesy of Geoscience Australia.

#### Hydrogeochemical impact analysis

Analysis of limited post-spill data provides no evidence to either support or refute that the Leach Tank 1 spill on 7 December 2013 entered the groundwater underlying the plant. This is due to the low flow rates, the similarity of the leachate with the groundwater underlying the plant area, the lack of information on the potential for leachate to infiltrate through the unsaturated zone into the groundwater system and the lack of post-spill groundwater-level measurements or water quality samples taken. In addition, it is likely to be difficult to assess the singular impact of the spill in the context of the pre-existing contamination underlying the plant area.

Leach tank discharge chemical results provided by ERA shows that the material has very high concentrations of sulfur, magnesium, manganese, iron and aluminium (Table 2.2). This can be considered to be equivalent to a magnesium-sulfate dominant fluid. Similar results were obtained in the Supervising Scientist’s analysis of the slurry material (Table 4.6). The leachate is likely to have a similar chemical signature to groundwater under the plant area (magnesium-sulfate dominant). This does not rule out the possibility that the leach tank spill has impacted the groundwater at bores 35 and 36 if, for instance, fracture flow allowed for faster travel times and minimal interaction with lime occurred then the observed compositions could be expected. The order of magnitude difference in concentrations between 2009 and 2013 may be due to the post-spill samples being collected in the transition from wet to dry season, such that wet season recharge had not yet diluted groundwater (Appendix A).

It is also important to consider the relatively low volume of leachate that potentially infiltrated into the groundwater system. Of the 1.4 million litres of Leach Tank 1 material released in the spill, most of this was removed from the surface or remained within the bund. Of the material that remained, a further amount flowed into RP2. A conservative estimate of 1 900 L of fluid may have remained at the surface over the more permeable grassed areas and had potential to infiltrate and interact with groundwater[1]. Based on the water table mapping described earlier, it is assumed that approximately half may have entered the northerly flow path, and half the southerly flow path. A leachate chemical composition similar to current (pre-existing and contaminated) groundwater might make it difficult to differentiate the extent of any impact from the spill.

A simple calculation based on K values and flow directions, not taking into account unsaturated zone flow or reactive transport, shows that for any leachate that may have infiltrated the groundwater system and reached bore OA11 (~180 m to the south of the edge of the spill extent), it could take between 60 and 1 800 days. Similarly it could take between 50 and 1 500 days for the bores to the west, and 15 to 370 days to reach RP2 (to the northwest) via a groundwater pathway. As discussed above, given the relatively small volume of leachate with the potential to enter the groundwater system, and that only a proportion of that will enter the southerly groundwater flow path, a hydrogeochemical response is unlikely to be detected from this particular incident.

It is however possible to infer the likely water-rock interactions which would take place as a result of the spill. ERA supplied leach tank material chemical data to GA in January 2014, which showed that the spill material had high concentrations of total iron, sulfate (using sulfur concentration as a proxy) and a pH of 1.2; it is possible that hydrated ferrous sulfate efflorescence would form in the unsaturated zone upon oxidation of ferric-oxyhydroxides or basic ferric sulfates. This process has the potential to immobilise some of the contaminants in the plume but, to confirm this, detailed mineralogical tests would need to be undertaken on unsaturated zone material from within the spill extent area.

#### Conclusions

There is insufficient post-spill data to either support or refute that the Leach Tank 1 spill in December 2013 entered the groundwater underlying the plant. This conclusion is based on data contained in the hydrogeochemical impact assessment.

From both long-term average water-level analysis and recent average seasonal water-level assessment, there is a persistent groundwater divide located beneath the plant site causing groundwater to flow from the plant area in a north-northwest direction towards RP2 and in a south-southeast direction towards Corridor Creek.

Groundwater underlying the plant area has previously been shown to be contaminated. Analysis by GA (Figure 4.28) supports previous conclusions that contamination from the plant area has remained slow moving with little advance noted since 2009.

While the surface water in the spill-affected area all flows to RP2, groundwater from the plant site flows to the north as well as to the south and south east. Groundwater flowing along the southerly flow path may have the hydraulic potential to interact with Corridor Creek and via this into Magela Creek under suitable flow conditions. The data available for this assessment shows that not enough is known about the interaction of the groundwater system with the surface water system in the Corridor Creek area. A paucity of groundwater-level and chemistry data has inhibited a more detailed and specific assessment of the Leach Tank 1 spill.

While it is concluded that this particular spill is unlikely to have impacted the offsite environment, the lack of groundwater understanding along the southerly flow path needs to be addressed. This includes a lack of understanding of the interaction between the local, shallow groundwater systems with the deeper, regional system. In particular, the role of geological structures, and their hydraulic properties, is not adequately quantified. Geological structures may also play a key role in connecting the groundwater and surface water systems in the region. The current limitations in data and knowledge will impact the predictive power of any numerical groundwater models created for the site.

## 4.3  Radiation Exposure

### 4.3.1  Initial gamma dose rate measurements

Figures 3.14 and 3.15 show that gamma dose rates had reduced in Zone 1 areas after the cleanup and the subsequent wash down that occurred on 11 December 2013. Gamma dose rates one day after the spill (before cleanup) measured adjacent to and within Zone 1 amounted to between 0.7 µSv hr-1at the south-western perimeter to 1.7–3.5 µSv hr-1along the road in the vicinity of the crusher conveyor, opposite the power station. These gamma dose rates reduced to around 0.5 µSv hr-1 at the south-western perimeter and around 1 µSv hr-1 along the road, with a maximum of 1.4 µSv hr-1measured within Zone 2. A drain leading to RP2 showed a gamma dose rate of 2.8 µSv hr-1, however, the dose rate was higher away from the drain indicating the source was most likely related to the embankment material.

It is important to note that the measured gamma dose rates are the sum of the signals from the ground, including any previously deposited material, and gamma radiation emitted from mineralised material in plant infrastructure adjacent to the measurement location. This can, for example, be seen in the measurements taken adjacent to the fine ore bin (3.1 and 5.5 µSv hr-1) or the clarifier (4 µSv hr-1). These areas were not impacted by any spill material but both fine ore bin and clarifier contain significant amounts of mineralised material leading to elevated external gamma dose rates measured in their immediate vicinity.

### 4.3.2  Assessment of radiation dose from the spilled material to ERA staff and contractors

#### 4.3.2.1  Radionuclide analyses results

The dried slurry samples were analysed on 7 February 2014 using the SSD HPGe detectors, after sufficient time was allowed for ingrowth of the radon decay products in the samples. Results for 238U and 226Ra are shown in Table 4.7.

Samples of the supernatant were also analysed for 226Ra in the SSD radioanalytical lab and for uranium using ICP-MS at a NATA accredited laboratory. The results of the analyses are given in Table 4.7.

Table 4.7 also shows the combined 238U and 226Ra activity concentration for the samples, assuming all activity (i.e. the activity in the dry sample and the supernatant) was retained in the dry sample after the spill. As expected, 238U and 226Ra are in secular equilibrium in the combined results of slurry and supernatant, and the average combined activity concentration in the dry spill material amounts to 21.6 Bq g-1. This results in a slightly higher ore-grade than the one given in Table 2.1, and has been used for the subsequent dose assessment.

Table 4.7  Results of radionuclide analysis in the slurry samples

|  | Dry slurry Bq g-1dry |  | Supernatant Bq L-1 |  | Total Bq g-1dry |  | U grade % |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sample ID | 238U | 226Ra | 238U | 226Ra | 238U | 226Ra | U3O8 |
| RM13080 | 9.9±0.4 | 21.9±0.1 | 15 400±1 500 | 141±6 | 20.7±2.3 | 22.0±0.3 | 0.20±0.01 |
| RM13081 | 9.1±0.4 | 22.6±0.1 | 14 500±1 500 | 142±5 | 21.2±2.6 | 22.7±0.4 | 0.21±0.01 |
| RM13082 | 8.7±0.2 | 22.1±0.1 | 16 000±1 600 | 222±7 | 20.8±2.5 | 22.3±0.3 | 0.21±0.01 |

#### 4.3.2.2  Area impacted by the spill

The spill impacted an area on site of approximately 1.475 ha, the majority of it onto earthed hardstand, bitumen roads and concrete bunded areas. A small grassed area was also impacted (Section 2.4).

Using a conservative estimate of the entire volume of material in Leach Tank 1 and the area impacted by the spill allows estimating the average thickness of wet slurry that deposited across the impacted area to 0.095 m. To determine the thickness of the dried lateritic material after deposition and evaporation of the associated liquid, a dry bulk density of the material of 1.6 g cm-3, typical for soils in the area, was used as the dry bulk density of the lateritic material. The measurements of weights of the samples received by SSD (Table 2.4) allowed the determination of the average dry/wet mass ratio of the material to 0.43.

The average areal activity concentration (Bq cm-2) of the deposited slurry is calculated, assuming that the material was evenly distributed throughout the impacted area. This is of course a simplification, but appropriate for the purpose of estimating average gamma doses to workers involved in the cleanup of the spill.

The average areal activity concentration (Bq cm-2) can be calculated as:

A[Bqm2] =dslurry∙Cslurry ∙ρslurry=dslurry∙Cdry∙mdrymwet ∙ρslurry				(1)

With:

dslurry:	average thickness of wet deposited slurry (cm)

Cslurry:	activity concentration of wet slurry (Bq g-1)

ρslurry:	density of the wet slurry (1.35 g cm-3)

Cdry:	activity concentration of dry slurry (Bq g-1)

mdry:	mass of dried slurry (g)

mslurry:	mass of wet slurry (g).

The areal activity concentration calculated with equation (1) should be the same once the deposited material has dried:

A[Bqm2] =ddry∙Cdry ∙ρdry∙															(2)

With:

ddry:	average thickness of dry slurry (cm)

Cdry:	activity concentration of dry slurry (Bq g-1)

ρdry:	density of dry slurry (1.6 g cm-3)

The average thickness of dry material, ddry, can thus be estimated using:

ddry=dslurry∙mdrymwet ∙ρslurryρdry														(3)

Consequently, the average thickness of dry material spilled during the incident across the 1.475 ha of impacted area amounted to approximately 3.5 cm.

#### 4.3.2.3  Modelling of the external gamma radiation pathway

The ResRad computer code (ResRad offsite Version 2.6) has been used to calculate gamma doses to people standing and working on the material spilled during the incident. It was assumed that the material had dried, and the contribution of background radiation (i.e. radiation from any material present before the spill or radiation from ore bins) was not considered in the modelling. The average activity concentration of 238U in equilibrium with its decay products was assumed to be 21.6 Bq g-1.

Figure 4.31 shows the external gamma dose rate received for various thicknesses of material deposited after the incident. Assuming an average thickness of the dried material of 3.5 cm, the average dose rate received by a worker standing on the material was 1.6 µSv hr-1.

Figure 4.31  Effective gamma dose rates for various thicknesses of dried material with an activity concentration of 238U in equilibrium with its decay products of 21.6 Bq g-1

The dotted line in Figure 4.31 shows the expected maximum dose rate from a slab of material with the same activity concentration but infinite thickness, calculated from conversion factors given in Saito & Jacob (1995) who estimated air kerma from natural occurring radionuclides 1 m above ground using Monte Carlo modelling. This maximum amounts to 7 µSv hr-1.

#### 4.3.2.4  Inhalation pathway

Table 4.8 shows conversion coefficients to calculate doses from the inhalation of radon decay products (RDP) and long lived alpha activity (LLAA) in dust. Worker and general public conversion coefficients are shown. Dust conversion coefficients were calculated using the recommended values given in ICRP 71 (1995) and ICRP 72 (1996). LLAA dose conversion coefficients for an activity median aerodynamic diameter (AMAD) of both 1 µm and 5 µm are given. Table 4.9 shows the breathing rates for a worker given in ICRP Publication 66 (ICRP 1994).

Table 4.8  Inhalation dose coefficients for radon decay products (RDP) and long lived alpha activity (LLAA) assuming an activity mean aerodynamic diameter (AMAD) of 5 µm and 0% radon retention in the crushed and leached material.

|  | RDP μSv·(μJ·h·m3)-1 | LLAA (µSv Bqα-1) 1 µm 5 µm |  |
| --- | --- | --- | --- |
| Worker | 1.4 | 7.8 | 5.5 |

Table 4.9  Breathing rates (m3 hr-1) for a male adult and worker for different physical activities.

|  | Resting, sitting | Light exercise | Heavy exercise |
| --- | --- | --- | --- |
| Worker | 0.54 | 1.5 | 3.0 |

##### Estimate of the radon decay product inhalation pathway

The ResRad computer code (ResRad Offsite, version 2.6) has been used to calculate the radon decay product inhalation dose rates to workers involved in the cleanup of the material. It was assumed that workers were working on top of the spilled material during clean up. A radon emanation coefficient for tailings of 0.3 (Strong & Levins 1982) and an average diffusion length for radon in the material of 1.0 m were assumed.

The results of the ResRad worker radon decay product inhalation dose modelling is shown in Figure 4.32. The average dose rate from RDP inhalation for a thickness of spilled material of 3.5 cm is only 0.005 µSv hr-1. The maximum dose rate on top of the material, assuming a thickness of 1 m is 0.13 µSv hr-1. This is much lower than the dose rates received from gamma radiation.

It is not surprising that the radon decay product inhalation pathway for workers associated with the spill cleanup is low. The average thickness of the material is only 3.5 cm across the 1.475 ha, and assuming a diffusion length of 1 m, the amount of radon exhaling from the surface of a 3.5 cm thick layer is only 3.4 % of the radon exhalation expected from a layer with the same activity concentration of 226Ra but infinite thickness. In addition, the radon equilibrium factor in air on top of the spilled material is low, as the radon exhaling from the spill is ‘young’ and consequently the dose from the inhalation of RDP is expected to be low as well.

Figure 4.32  Dose rate from the inhalation of radon decay products for various thicknesses of dried material with an activity concentration of 238U of 21.6 Bq g-1 in radioactive equilibrium with its decay products. Dose rates were modelled using the ResRad computer code and assuming a worker is standing on top of the spilled material and assuming a low wind speed of < 1 m s-1 and atmospheric stability class A.

##### Estimate of the dust inhalation pathway

Dust LLAA data have been provided by ERA. The dust samples were collected using personal dust pumps attached to the bobcats involved in the clean up. Figure 4.33 shows the histogram and cumulative frequency plot of the measured LLAA concentrations (in Bq m-3).

The typical LLAA concentrations measured during the cleanup amounts to 11.4 mBq m-3. The 95th percentile LLAA concentration was 64.4 mBq m-3.

Figure 4.33  Histogram (left) and cumulative probability (right) of long lived alpha activity concentrations measured during the cleanup of the spill

Equation 4 is used to calculate the dose rates to workers from the inhalation of dust generated during the cleanup. The dose conversion factor used and the breathing rate (light exercise) were taken from Tables 4.8 and 4.9.

It was assumed that radionuclides are in equilibrium with 238U down to 226Ra, but that all radon in the dust particles was lost as a result of the crushing and leaching process. In addition, although it can reasonably be assumed that the AMAD of the dust inhaled during clean up would be greater than 1 µm, due to the dust creating activities (scraping and dumping) taking place immediately next to the bobcat, an AMAD of the aerosol inhaled of 1 µm was used for the calculations, which leads to a conservative dose estimate.

Edust=DCF∙LLAA∙BR															(4)

With:

DCF:	7.8 µSv Bqα-1

LLAA:	0.0114 (0.0644) Bq m-3

BR:		1.5 m3 hr-1

Consequently, the typical dust inhalation dose rate during cleanup equals 0.13 µSv hr-1. The 95th percentile dust inhalation dose rate amounts to 0.75 µSv hr-1. It is important to note that this assessment does not include any protection factors associated with the wearing of dust masks during the cleanup and thus actual exposure to workers is expected to be lower.

#### 4.3.2.5  Exposure scenario

Table 4.10 shows the typical and maximum dose rates from the three exposure pathways, external gamma radiation, radon decay product inhalation and dust inhalation. Approximately 90% of the dose received by workers involved in the cleanup of the spill is due to exposure to gamma radiation.

Table 4.10  Dose rates [µSv hr-1] estimated for workers involved in the cleanup.

|  | γ-radiation | Dust inhalation | RDP inhalation | Total |
| --- | --- | --- | --- | --- |
| Typical | 1.6 | 0.13 | 0.005 | 1.73 |
| Max | 7 | 0.75 | 0.13 | 7.88 |

To calculate doses received by workers during the cleanup, the following scenario has been assumed: workers involved in the cleanup worked in 12 hour shifts with 10 hours were spent on the spilled material. The initial cleanup, with the exception of the exclusion zone around the failed tank, occurred over 4 days. This scenario results in a total of 40 hours exposure time and thus a typical dose of 0.07 mSv, and a maximum dose of 0.32 mSv received by the workers.

Mean annual radiation doses for 2013 to workers working in the area where the spill occurred (Radiation area R6: mill) are shown in Table 4.11 and the doses are compared with the additional doses received during the cleanup.

Table 4.11  Mean annual doses (in mSv) received by workers in the Processing Production working group in 2013 (ERA 2014) and estimated doses (in mSv) received during the cleanup operation.

|  |  | γ-radiation | Dust inhalation | RDP inhalation | Total |
| --- | --- | --- | --- | --- | --- |
| Processing Production Annual Dose | Mean | 1.8 | 0.09 | 0.12 | 2.01 |
| Cleanup Operation | Typical | 0.06 | 0.005 | 0.00 | 0.065 |
|  | Max | 0.28 | 0.03 | 0.005 | 0.315 |

Assuming a worst case exposure, 0.32 mSv would have been received by workers during the cleanup in addition to the mean annual effective dose of 2.01 mSv received by the Processing Production working group in 2013. This contribution to the total annual dose is small in comparison to the annual worker dose limit of 20 mSv and of no concern to the health of workers involved in the cleanup of the spill. The maximum dose from the cleanup operation is approximately 5% of the maximum annual dose received by a worker at ERA in 2013 (6.5 mSv).

### 4.3.3  Assessment of radiological impacts to the public

#### 4.3.3.1  Background

The main airborne constituents that can add to the inhalation radiation dose received by the public in the vicinity of a uranium mine are RDP in air and LLAA radionuclides contained in dust.

RDP are the short-lived decay products of 222Rn (radon), a naturally occurring radioactive gas that is formed from the decay of 226Ra in the 238U decay series (Figure 4.34) and that exhales from the ground surface (soils and rocks) to the atmosphere by natural processes.

LLAA radionuclides are the long half-life alpha-emitting radionuclides in the 238U decay series (Figure 4.34). They are particle bound and enter the atmosphere when dust is stirred up from the ground surface by natural processes and human activities.

Figure 4.34  Uranium-238 decay series showing RDP (red) and LLAA radionuclides (brown).

The concentration of radon and RDP in air depends on several factors:

soil properties (e.g. moisture content, porosity, 226Ra content), which affect radon exhalation from the ground surface to the atmosphere

meteorological conditions (e.g. rainfall, temperature, pressure), which can also affect radon exhalation from the ground surface to the atmosphere

wind speed, which affects atmospheric dispersion of radon and radon progeny

wind direction, which determines the regional source term of radon in air

how long the radon in air has been decaying for (i.e. the ‘age’ of radon in air), since RDP grow-in from the decay of radon

The concentration of LLAA radionuclides in dust also depends on several factors:

238U activity concentration in soil

rainfall, which reduces re-suspension and washes out dust from the atmosphere

wind speed, which generally increases dust generation

human activities such as mining, which can increase dusts via ground disturbance

SSD routinely monitors RDP and dust LLAA concentrations at Jabiru East and Jabiru Town. The purpose is to provide public assurance that there is no unacceptable radiation risk via the inhalation pathway from exposure to mine-related sources of RDP and dust LLAA radionuclides. SSD’s RDP and dust monitors were operational at the time of the leach tank incident.

#### 4.3.3.2  Spilled material as an additional exposure source to the public

##### Spill material in the context of existing mine as a source of radon and dust

The spilled material had an estimated initial footprint of 1.475 ha and average thickness of 3.5 cm (Section 2.4). Cleanup of spilled material was largely completed by two weeks after the incident. By comparison, ore and waste rock stockpiles at Ranger mine have an estimated total footprint 100 times larger than that of the spilled material and thickness of several metres to several tens of metres. Effectively no change in size of the stockpiles occurred in the two weeks following the incident.

The following assumptions have been applied to provide context on the spilled material and stockpiles as comparative sources of radon and LLAA radionuclides:

average 238U concentration of stockpiles is half that of spilled material

222Rn diffusion length of spilled material is 1 m, similar to that for soils

stockpile radon diffusion length is 10 m (Lawrence 2005) and average height is 25 m

dust re-suspension factor of the spilled and stockpiled material is the same.

The percentage of radon exhalation from a material of thickness x (relative to infinite thickness) and diffusion length D can be described by the relationship:

1-e-x/D×100%

Radon exhalation from the spilled material with 3.5 cm thickness would be around 3.4% relative to infinite thickness and that from the stockpiles with 25 m height would be around 92% relative to infinite thickness. This, together with estimates on comparative footprints and 238U activity concentrations, implies that radon exhalation from the spilled material would be more than 1000 times less than that from the stockpiles.

With regard to dust, the total dust LLAA load from the spilled material would be around 50 times less than that from the stockpiles over the two week period until cleanup was complete.

##### Transport pathway for offsite impacts to the public

Wind direction determines the transport pathway of radon progeny and dust in air and the potential for public exposures to mine-related sources. It is assumed that radon progeny in air at Jabiru Town includes a mine-related component when the wind is from the 90°–110° sector. The same assumption is made for Jabiru East when the wind is from the 110°–180° sector. Analysis of half-hourly wind direction data from the Bureau of Meteorology (BoM) weather station at Jabiru Airport (Figure 4.35) indicated that the wind was from the direction of the mine for 53 half-hour periods at Jabiru East and for 54 half-hour periods at Jabiru Town during the two weeks after the incident. This suggests that there was potential for RDP and dust LLAA originating from the spilled material to be transported in the direction of Jabiru Town and Jabiru East, though it is unlikely to have been distinguishable above that originating from the stockpiles due to source size considerations.

Figure 4.35  Frequency histogram of wind direction data from the BoM weather station at Jabiru Airport for the two weeks after the incident (7–20 December 2013). The circumferential axis shows wind direction in ten degree sectors. The radial axis shows the number of half-hourly periods that the wind was from each sector. The blue shaded sector represents the direction of Jabiru Town from the Ranger mine and the red shaded sector represents the direction of Jabiru East from the Ranger mine. A wind direction of 0 indicates still conditions (i.e. no wind).

#### 4.3.3.3  Monitoring methods

Environmental RDP monitors manufactured by Radiation Detection Systems were used for continuous monitoring RDP concentrations in air. The monitors operated at a flow rate of 0.35 L min-1 drawing air through a Whatman GF/C filter positioned above an alpha counter. Hourly concentration data was logged in the internal memory of the monitors, which were downloaded at approximately fortnightly intervals by SSD staff based at the JFS.

EcoTech MicroVol-1100 low flow-rate air samplers were used for dust sampling. The samplers operated at a flow rate of approximately 3 L min-1 drawing air through a Whatman GF/C filter. Filters were changed at approximately fortnightly intervals by SSD staff based at the JFS and sent to SSD laboratories in Darwin for analysis of LLAA using Daybreak 582 alpha counters. A delay period of nominally 14 days between the end of sample collection and start of counting was applied to allow short-lived alpha activity radionuclides on the filter to decay. Count times were typically three to four days to ensure reasonable counting statistics. Measurement of the background alpha activity of the counters was made prior to analysis of each filter. Counter efficiency was determined by counting a standard alpha disk source.

#### 4.3.3.4  Monitoring results

##### Radon progeny

Figure 4.36 shows the hourly radon progeny monitoring data from Jabiru East and Jabiru Town and the hourly rainfall data from the BoM weather station at Jabiru Airport from two weeks before to two weeks after the incident.

RDP concentrations in air at Jabiru East and Jabiru Town showed typical and in phase diurnal variations. Concentrations generally built up in the early morning and peaked around 6–9 am under conditions of low wind speed and then decreased during the day with increasing wind speed (Figure 4.37). The effect of increasing wind speed is to mix radon exhaled from the ground into a larger atmospheric volume and thereby decrease the concentration of RDP in surface air.

Figure 4.36  Hourly RDP monitoring data and hourly rainfall data from two weeks before to two weeks after the incident.

Figure 4.37  Average hourly radon progeny concentration and average hourly wind speed for the four week period from two weeks before to two weeks after the incident.

Rainfall was generally confined to intermittent storms and showers and does not appear to have had a strong influence on radon progeny concentrations. Most likely there was no substantial and sustained increase in soil moisture content from rainfall during the period to suppress regional radon exhalation to any large extent.

Figure 4.38 shows a comparison of the average hourly radon concentrations in air at Jabiru Town and Jabiru East for the two weeks before (23 November–6 December 2013) and two weeks after (7–20 December 2013) the incident. Table 4.12 gives the mean and standard deviation of the average hourly concentrations. T-test analysis of the data indicated that there was no significant difference between the mean of the hourly average concentrations during the two weeks before and after the incident at either Jabiru East or Jabiru Town (p < 0.05).

Figure 4.38  Comparison of average hourly radon progeny concentrations in air for the two weeks before (grey line) and two weeks after (black line) the incident.

Table 4.12  Mean and standard deviation of average hourly radon progeny concentrations in air at Jabiru Town and Jabiru East in the two weeks before and two weeks after the incident.

| Location | PAEC before (µJ m-3) | PAEC after (µJ m-3) |
| --- | --- | --- |
| Jabiru Town | 0.027 ± 0.021 | 0.029 ± 0.013 |
| Jabiru East | 0.053 ± 0.038 | 0.063 ± 0.041 |

##### Long Lived Alpha Activity in dust

Figure 4.39 shows the LLAA monitoring data from Jabiru East and Jabiru Town from approximately two weeks before to two weeks after the incident. One measurement was made completely before and one completely after the incident and one measurement was made from eight days before to four days after the incident at both locations. The data showed no unusual changes in LLAA concentrations following the incident above the normal variability that occurs from sampling period to sampling period due to differences in prevailing meteorological conditions. The measured concentrations were also typical of those in previous wet seasons and less than typical dry season concentrations (Supervising Scientist 2013).

Figure 4.39  LLAA concentrations measured in dust from approximately two weeks before to two weeks after the incident. The dotted lines represent two standard deviations of the measured value based on counting statistics.

#### 4.3.3.5  Conclusions

Consideration of the spilled material in the context of existing ore and waste rock stockpiles at Ranger mine suggested that it would be an effectively negligible mine-related source of radon progeny in air and LLAA radionuclides in dust. Results of atmospheric monitoring conducted by SSD indicated that there were no unusual increases in radon progeny or LLAA in dust concentrations in air at Jabiru Town or Jabiru East following the incident. This implies that there was no increased radiation risk to the public at Jabiru Town or Jabiru East from radon progeny or LLAA in dust associated with the spilled material.

# 5  Conclusions

It is concluded, based upon extensive surface water, groundwater and radiological analysis, that the failure of Leach Tank 1 at the Ranger uranium mine on 7 December 2013 did not cause any adverse impact to the offsite environment, including Kakadu National Park, nor cause any impact to the health of local residents or mine workers.

## 5.1  Surface water

It is concluded that the Ranger uranium mine leach tank incident of 7 December 2013 did not cause any impact to surface waters off the operational Ranger mine-site, including Kakadu National Park.

Chemical and biological monitoring conducted by the Supervising Scientist in Magela Creek both prior to, and following, the incident included continuous conductivity and pH, manual and automated sample collection for chemistry analysis and in situ toxicity testing. The cumulative results of these monitoring programs indicate no change in water quality in Magela Creek downstream of the Ranger uranium mine as a result of the leach tank failure.

Based upon inspections of the site and the extent of the spill there was no mechanism for leach slurry, or its derivatives, to have left the mine-site area and entered the surrounding environment via the surface water pathway. It was determined that the leach slurry released during the incident remained within the plant area, with an unknown quantity reporting via the storm water system to RP2. The slurry residue observed at the storm water outflow indicated a rapid flow of slurry following the incident and, whilst the volume of slurry which reported to RP2 cannot be determined, it was insufficient to affect water quality in the pond. It is likely that the flow was brief but none the less it must be concluded that a substantial volume did enter the pond.

It is noted that the release of a substantial volume of process material to the pond water system is not in accordance with section 3.4 of the Environmental Requirements of the Commonwealth of Australia for the operation of the Ranger Uranium Mine which states;

3.4  Process water must be totally contained within a closed system except for:

(a)  losses through natural or enhanced evaporation;

(b)  seepage of a quality and quantity that will not cause detrimental environmental impact outside the Ranger Project Area; and

(c)  subject to clauses 3.1, 3.2 and 3.3, process water which has been treated to achieve a quality which:

i)   conforms to a standard  practice or procedure recommended by the Supervising Scientist; and

ii)  is not less than that of the water to which it is to be discharged.

Based upon site inspections and the analysis of samples collected following each phase of the cleanup operation it was determined that the spill area could be returned to the pond water catchment. Following the cleanup works it is not expected that the spill will have any ongoing impact on pond water quality at the Ranger uranium mine, and the current program of routine monitoring is sufficient to detect any changes should they occur. The spill did not result in any adverse impact to offsite water quality, including within Kakadu National Park, nor cause any impact to the health of local residents or mine workers.

## 5.2  Groundwater and soils

The Supervising Scientist commissioned Geoscience Australia to investigate potential impacts to groundwater as a result of the leach tank incident.

It is noted that limited historic groundwater data available in the area of the spill, and the 6 week timeframe for Energy Resources of Australia Ltd to commence the requested groundwater monitoring program, constrain the level of analysis which can be undertaken. The delay was disappointing and it is hoped future requests will be actioned in a timelier manner. Despite these limitations sufficient information is available, including soil profiling work, to conclude that impacts to groundwater beneath the immediate spill area would be minimal, particularly in the context of pre-existing groundwater conditions.

The high rate of soil compaction and low residence time of the slurry on the surface would have restricted the infiltration of contaminants into the groundwater system. If any contaminants were to have infiltrated, the low volume is unlikely to alter the existing hydrogeochemistry of the system, particularly in the context of pre-existing groundwater conditions beneath the plant.  The work of Geoscience Australia supports previous studies indicating that groundwater flow rates from the plant area are likely to be low, with a correspondingly low likelihood of any significant contaminant movement away from the plant area. It should be noted, however, that particular geological structures may significantly enhance flow rate in some instances, and further information in this regard is needed in the Corridor Creek area. A greater understanding of the groundwater system in this area will assist in the remediation of existing groundwater contamination beneath the plant during site rehabilitation.

Historical and recent groundwater data indicate a groundwater divide exists beneath the plant area, with groundwater flowing both to the north and south. The nearest receptor is Corridor Creek, approximately 500 meters to the south-east of the spill location, and a further 1 km from the mining lease boundary. Whilst there is likely to be connectivity between Corridor Creek and the groundwater system, due to the dilution which will occur over that distance, and within the creek itself, it is highly unlikely that the spill would result in any measurable concentrations of solutes being transported offsite via the groundwater-surface water pathway.

It is noted that soil sampling within the mine footprint has not occurred since 2007. A soil contamination monitoring programme should be re-introduced. In doing so due consideration needs to be given to the technical challenges in designing a program to reliably evaluate the existing contamination during the operational phase of the mine, while providing benchmark data for closure planning.

## 5.3  Radiation exposure

Based upon analysis of leach slurry samples and radiological monitoring results the Supervising Scientist Division has assessed the likely dose to workers involved in cleaning up the leach slurry and to residents in the surrounding area.

Cumulative effective dose to workers involved in the clean up was estimated to be typically in the order of 0.07 mSv and a maximum of 0.32 mSv. This compares with the mean annual effective dose to Processing Production workers of 2 mSv per year and the annual dose limit for workers of 20 mSv per year.

Results of atmospheric monitoring conducted by Supervising Scientist Division indicated that there were no unusual increases in radionuclide concentrations in air at Jabiru Town or Jabiru East following the incident.

It is concluded that the incident did not result in any increased radiation risk to members of the public and that doses to workers involved in the cleanup operation were small in comparison to mean annual worker doses.

# 6  Recommendations

1.    It is recommended that Energy Resources of Australia Ltd provide the Ranger Minesite Technical Committee with an implementation plan to address the recommendations of the Geoscience Australia report, including:

- an increase in the frequency and density of routine groundwater monitoring in both the plant area and the Corridor Creek region

- investigate the role of geological structures in groundwater movement to the east of the plant area

- continue the development and maintenance of a spatial database of groundwater data for the Ranger uranium mine, and

2.   It is recommended that soil contamination investigation works undertaken by Energy   Resources of Australia Ltd in 2006 and 2007 be revisited to better inform site closure planning.

# References

Akber R, Lu P, Bollhöfer A & Gellert C 2011. Radioactivity in land application areas estimated from historic water monitoring data. Energy Resources of Australia Ltd - Ranger Mine.

Alarcon Leon E, Gellert C & Pillai M 2007a. Groundwater contamination in the Ranger mine plant area - Phase 2 investigations for ERA Ranger Mine. EWL Sciences.

Alarcon Leon E, Gellert C & Puhalovich A 2007b. Position Paper: Current Status of Contaminated Sites at Ranger Mine and Proposed Way Forward. EWL Sciences.

Anon 1975. Munsell® Soil Color Charts. Frank McCarthy Color Pty Ltd, Kew.

Chartres CJ, Walker PH, Willett IR, East TJ, Cull RF, Talsma T & Bond WJ 1991. Soils and hydrology of Ranger Uranium Mine sites in relation to application of retention pond water. Technical Memorandum 34, Supervising Scientist for the Alligator Rivers Region, AGPS, Canberra.

ERA 2013. ERA Ranger water management plan 2013–14. Energy Resources of Australia Ltd – Ranger Mine. RWMP001.

ERA 2014. Radiation Protection and Atmospheric Monitoring Program: Report for the Year ending 31 December 2013. Energy Resources of Australia Ltd – Ranger Mine. RSRP-1304–01.

Esparon A & Pfitzner J 2010. Visual gamma: eriss gamma analysis technical manual. Internal Report 539, December, Supervising Scientist, Darwin. Unpublished paper.

Gellert C 2009. Ranger Contaminated Sites Investigation: 2008 Groundwater Sampling for ERA Ranger Mine. EWL Sciences.

Gellert C & Jones C 2008. Status of Contaminated Sites at the Ranger Mine as of December, 2007. EWL Sciences.

Golder Associates Pty Ltd. 2011. Initial three-dimensional solute transport modelling of the Ranger Uranium Mine tailings dam. Golder Associates Pty Ltd.

Harford A, Trenfield M, Cheng K & van Dam RA 2014. Ecotoxicological assessment of manganese. Internal Report 630. April, Supervising Scientist, Darwin. Unpublished paper.

Hogan, A, van Dam RA, Houston MA, Harford AJ & Nou S 2010. Uranium exposure to the tropical duckweed, Lemna aequinoctialis, and pulmonate snail, Amerianna cumingi: fate and toxicity. Archives of Environmental Contamination and Toxicology 59, 204–215.

Hollingsworth I 2006. Contaminated Soil Investigation Ranger mine for ERA Ranger Mine by EWL Sciences Pty Ltd. EWL Sciences Report.

ICRP 1994. Human respiratory tract model for radiological protection. ICRP Publication 66, Annals of the ICRP 24(1–3).

ICRP 1995. Age-dependent Doses to Members of the Public from Intake of Radionuclides - Part 4 Inhalation Dose Coefficients. ICRP Publication 71. Annals of the ICRP 25(3–4).

ICRP 1996. Age-dependent doses to members of the public from intake of radionuclides: Part 5 compilation of ingestion and inhalation dose coefficients. ICRP Publication 72, Annals of the ICRP 26(1).

Iles M 2004. Water quality objectives for Magela Creek - revised November 2004. Internal Report 489, December, Supervising Scientist, Darwin. Unpublished paper.

Klessa DA 2001. A review of groundwater chemistry monitoring data at Ranger. Internal Report 363, Supervising Scientist, Darwin, Unpublished paper.

Lawrence C 2005. Measurement of 222Rn exhalation rates and 210Pb deposition rates in a tropical environment. PhD thesis, Queensland University of Technology, Brisbane.

McDonald RC & Isbell RF 2009. Soil profile. In: The National Committee on Soil and Terrain, Australian Soil and Land Survey Field Handbook. Third Edition, CSIRO Publishing, Collingwood, 147–204.

Medley P, Bollhöfer A, Iles M, Ryan B & Martin P 2005. Barium sulphate method for radium-226 analysis by alpha spectrometry. Internal Report 501, June, Supervising Scientist, Darwin. Unpublished paper.

Murray AS, Marten R, Johnston A & Martin P 1987. Analysis for naturally occurring radionuclides at environmental concentrations by gamma spectrometry. Journal of Radioanalytical and Nuclear Chemistry, Articles 115, 263–288.

Noller BN, Currey NA, Ayers GP & Gillett RW 1990. Chemical composition and acidity of rainfall in the Alligator Rivers Region, Northern Territory, Australia. Science of the Total Environment 91, 23–48.

Office of the Supervising Scientist 2002. Water release standards in the Alligator Rivers Region: An assessment by the Alligator Rivers Region Research Institute (reprint of historic document). Internal Report 397, December, Supervising Scientist, Darwin. Unpublished paper.

Pfitzner J 2010. eriss HPGe detector calibration. Internal Report 576, October, Supervising Scientist, Darwin. Unpublished paper.

Puhalovich A 2010. Evolution of conceptual hydrogeological models, Ranger Uranium Mine, Northern Territory. Groundwater 2010.

Saito K & Jacob P 1995. Gamma ray fields in the air due to sources in the ground. Radiation Protection Dosimetry 58, 29–45.

Salama R and Foley G 1997. Ranger Regional Hydrogeology Conceptual Model. Report Prepared for ERA Ranger Mine. CSIRO Land and Water.

Saynor MJ, Evans KG, Smith BL, Crisp E & Fox G 2001. Field monitoring information for the Swift (Ngarradj) Creek catchment Northern Territory. Internal Report 355, Supervising Scientist, Darwin. Unpublished paper.

Strong KP & Levins D M 1982. Effects of moisture content on radon emanation from uranium ore and tailing. Health Physics 42, 27–32.

Supervising Scientist 2005. Annual Report 2004–05. Supervising Scientist, Darwin NT.

Supervising Scientist 2008. Annual Report 2007–08. Supervising Scientist, Darwin NT.

Supervising Scientist 2010. Annual Report 2009–10. Supervising Scientist, Darwin NT.

Supervising Scientist Division 2012. Surface water chemistry monitoring protocol to assess impacts from the Ranger Mine. Internal Report 609, December, Supervising Scientist, Darwin. Unpublished paper.

Supervising Scientist 2013. Annual Report 2012–13. Supervising Scientist, Darwin NT.

van Dam RA, McCullough CD, Hogan AC, Houston MA, Harford AJ & Humphrey CL 2010. Aquatic toxicity of magnesium sulphate, and the influence of calcium, in very low ionic concentration water. Environmental Toxicology & Chemistry 29, 410–421.

Weaver T, O'Neill A, Makin S, Murfitt T, Berryman S & McGowan P 2010. Independent hydrogeological review Tailings Storage Facility Ranger uranium mine. URS report for Energy Resources of Australia Ltd. Report no. 43295269.

Wells MR 1979. Soil Studies in the Magela Creek Catchment 1978. Part 1. Land Conservation Unit LC79/1A, Territory Parks and Wildlife Commission, Darwin.

White LA & McLeod PJ 1985. Soils of the Ranger Monitoring Area. Technical memorandum 85/4. Conservation Commission of the Northern Territory, Darwin.

[1] This estimate is based on the assumption that the spill was 10 cm deep over 30 m2 of the spill extent area amenable to infiltration (vegetation or unsealed and uncompacted ground) gives 3 000 L of slurry. The slurry is 37% solid material, 63% liquid. This yields 1 900 L of liquid at the surface which had a chance to infiltrate the soil.

The equilibrium factor for a non-equilibrium mixture of short-lived radon decay products in air is defined as the ratio of the activity concentration of radon in radioactive equilibrium with its short-lived decay products (Ceq) with the same potential alpha activity concentration as the non-equilibrium mixture of short-lived radon decay products associated with the measured radon activity concentration in air (C0): E =  Ceq/C0